## Rfi
RFI Log
View: | Export View
Project Number: | S590.
Project Name: | ST. GEORGE TEMPLE
Number |  | Rev | Spec Section | Drawing Ref | Type | Subject | Question | Suggestion | Responses | Ball In Court | Ball In Court Organization | Priority | From | From Organization | To | To Organization | Sent | Reference | Schedule | Cost | ROM | State | Due By | Answer Marked On | Responded On | Forwarded On | Created Date | Status
1 |  | 1 | 034100 |  | Request for Information | Precast Questions Dimensions & Elevations | Question from RFI 1 response: Ref: attached layout 1.Grid A5.3 and AH- No opening shown on plan. Panel Q shows a door opening. Advice? 2.Grid A5.5 and AH- there is no F panel, should this be panel P? 3.Grid A8 between AC-AB and AG-AF- the dimensions add up to 27'-11 1/14" grid to grid. It should be 28'-0". Please advise where to add the 3/4"? |  | See Attached "RFI 1A - CRSA Response" |  |  | Medium | Brent Klopfer | Forterra Structural Precast | CRSA ARCHITECTURE |  | 09/17/2019 |  |  |  |  | Closed | 09/19/2019 | 09/26/2019 | 09/17/2019 |  | 09/17/2019
2 |  | 0 | 220716 |  | Request for Information | LEED Submittal Removal | Please confirm that per a phone conversation between David Adams and Scott Gilberg on 9-11-2019 that this is not a LEED project and the references in sections 220716, 220719, 221116, 224716, 230713, 230716, 232113, 233300, 233600, 236423 and 238240 calling for LEED submittals can be removed. For reference I have attached a list of the specific submittals. |  | confirmed this project is not a LEED project. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 09/12/2019 |  |  |  |  | Closed | 09/17/2019 | 09/19/2019 | 09/19/2019 |  | 09/12/2019
3 |  | 0 |  |  | Request for Information | Panels Tilt Bracing | 1. Panel Tilt Braces will be anchored to the suspended deck . The typical brace will impose an uplift load of between 1700 lbs and 2000 lbs for the shorter walls, where the taller entrance panels will have about a 3000 lb uplift force. Due to the deck thickness, tilt brace anchors will need to be drill through the slab and deck with a possible backing plate. Please confirm acceptance? |  | It is acceptable to drill though the concrete and metal deck and use a backing plate. Coordinate with Westland for the repair of the holes after the bracing and anchors are removed. ¦ ¦ Westland Construction needs to coordinate what is required for repairing holes after bracing is removed. The repairing of the holes if not included in our price and will need to be review if we're required to repair. |  |  | Medium | Brent Klopfer | Forterra Structural Precast | David Adams | Westland Construction, Inc. | 09/26/2019 |  |  |  |  | Closed | 10/01/2019 | 10/15/2019 | 09/26/2019 | 10/10/2019 | 09/26/2019
4 |  | 0 |  |  | Request for Information | Plan Review Questions | Please see the attached list of questions. If there is any ambiguity or questions arising from them please let me know. |  | See attached for answered structural questions ¦ See attachment ¦ See completed RFI. ¦ ¦ looks like we are still needing a response to the question regarding Sheet P110. |  |  | Medium | David Adams | Westland Construction, Inc. | Kyle Welch | CRSA ARCHITECTURE | 10/10/2019 |  |  |  |  | Closed | 10/15/2019 | 10/30/2019 | 10/30/2019 | 10/29/2019 | 10/10/2019
5 |  | 0 |  |  | Request for Information | precast openings | PLEASE PROVIDE THE FOLLOWING INFORMATION: 1. Do the the windows clouded in the attached elevation have the back forming like the walk through openings have? 2. Please confirm the opening size? With the dimensions that are shown on the elevations and details we come up with a clear opening of 4'-0 1/2"? See attached PDF. |  | Yes, the windows above the openings will be back formed as well 4'-0 1/2" is Correct for clear opening width These have also been noted in the review of the Shop Drawings ¦ |  |  | Medium | Brent Klopfer | Forterra Structural Precast | CRSA ARCHITECTURE |  | 10/15/2019 |  |  |  |  | Closed | 10/23/2019 | 10/21/2019 | 10/21/2019 | 10/18/2019 | 10/15/2019
6 |  | 0 |  |  | Request for Information | AE 4136 Elevations | Please advise if the elevations for called out as RM 176 on Sheet 4136 are supposed to be the elevations for RM 183, and the elevations called out for RM 175 and 191 are for RM 184? |  | You are Correct. Only Rooms 183 & 184 are on this sheet with the coordinating elevations. This was previously caught by CRSA and fixed. Room names and numbers have been revised. Updated sheet will be released with Addendum #6 |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/21/2019 |  |  |  |  | Closed | 10/26/2019 | 10/24/2019 | 10/21/2019 |  | 10/21/2019
7 |  | 0 |  |  | Request for Information | Tie Rods | Can we sleeve the tie rod holes and post install the bolts after we pour the jacket walls? We could sleeve with pipe 1/8" bigger than bolts, or as tight as we can get them hoping to eliminate the need of grouting. If approved could we use schedule 40 or 80 PVC for sleeves? |  | SEE ATTACHMENT ¦ |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | Structural Engineers |  | 10/24/2019 |  |  |  |  | Closed | 10/27/2019 | 10/30/2019 | 10/28/2019 | 10/24/2019 | 10/24/2019
8 |  | 0 |  | Sheet S220 | Request for Information | Core Elevator & Stairwell Walls | We could sleeve with pipe 1/8" bigger than bolts, or as tight as we can get them hoping to eliminate the need of grouting. As per our meeting, we discussed pouring continuous walls and tying the suspended slabs in with form savers, can we get details and engineering showing this? Also, please clarify the note on detail 16-S220 stating 125% of dowel when using form saver. |  | See attached for our response ¦ |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | Structural Engineers |  | 10/24/2019 |  |  |  |  | Closed | 10/27/2019 | 10/30/2019 | 10/29/2019 | 10/24/2019 | 10/24/2019
9 |  | 0 |  | AE100 and S100 | Request for Information | Discrepancy in Structural & Architectural Pages | We could sleeve with pipe 1/8" bigger than bolts, or as tight as we can get them hoping to eliminate the need of grouting. Page AE100 shows 2 Walls and S100 shows 1 Wall (Grid A-H A.5 to A.2) Please Clarify |  | These are existing walls to remain. There is the existing Annex foundation wall and then an existing wall to support the concrete lid of the Chiller project completed in 2015. No new concrete walls will be poured along Grid AH between A2 - A5 |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 10/24/2019 |  |  |  |  | Closed | 10/27/2019 | 10/28/2019 | 10/28/2019 |  | 10/24/2019
10 |  | 0 |  | Sheet S242 | Request for Information | New Details for Jacket Walls | As per owners request detail 3-S242 needs to change showing us pouring the jacket walls before the Matt Slab. |  | See Attachment ¦ |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | Structural Engineers |  | 10/24/2019 |  |  |  |  | Closed | 10/27/2019 | 10/30/2019 | 10/28/2019 | 10/24/2019 | 10/24/2019
11 |  | 0 |  |  | Request for Information | Micropiles Location | For the interior micropiles, we should plan for the center of the proposed micropiles being 20 – 22” off of the existing columns or foundation walls. For the exterior micropiles we will use a bigger drill, which will require approximately 24” off of the face of the adjacent foundation walls. |  | Details will be revised to accommodate the clearance needed. These modified details will be included in a forthcoming addendum. ¦ Drawings have been revised in CCD #2. See attached. ¦ ¦ ¦ ¦ |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Structural Engineers |  | 11/05/2019 |  | 1 | 1.00 |  | Closed | 10/27/2019 | 12/04/2019 | 11/21/2019 | 11/14/2019 | 10/24/2019
12 |  | 0 |  |  | Request for Information | Underpinning Pier Location | As per our conversation with the mico pier contractor, the locations will change resulting in longer Needle Beams and Tie Rods, this will also increase the wall thickness and location. Can we get some clarification on this? | This RFI is going to be tied with RFI - 011 | See attached for ARW Response ¦ Drawings have been revised and are issued as CCD #2. See attached drawings ¦ ¦ |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | Structural Engineers |  | 11/05/2019 |  | 1 | 1.00 |  | Closed | 10/27/2019 | 12/04/2019 | 11/21/2019 | 11/14/2019 | 10/24/2019
13 |  | 0 |  | Sheet S211 | Request for Information | Compressible Sealant | On Sheet S211 Detail 13 it calls for a Compressible Sealant. We have looked through the plans and specifications and can’t find what that material consists of. Please advise. |  | See Attachment. Additional response required by Architect. ¦ Correct me if I am wrong, but isn't this detail specific to the Cogen intake wells. With the removal of the Cogens, this detail is now not used. Can you think of any other location where the buried concrete lid does not want to bear on concrete walls below? |  |  | Medium | Aaron Bolli | Innovative Concrete LLC | Structural Engineers |  | 10/24/2019 |  |  |  |  | Closed | 10/27/2019 | 10/30/2019 | 10/28/2019 | 10/25/2019 | 10/24/2019
14 |  | 0 |  |  | Request for Information | Interior Signage Plan | Upon review of the preliminary signage layout we have highlighted areas in the attached signage layout that may need additional signs. Please advise if the highlighted areas need to have signs placed there. If so please designate the verbiage and layout that will be desired for the location. |  | Westland's markups were sent back to the owner for review/clarification. Crys Briggs has made the appropriate revisions. See updated plans. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/29/2019 |  |  |  |  | Closed | 11/29/2019 | 11/08/2019 | 11/08/2019 |  | 10/29/2019
15 |  | 0 | 233113 |  | Request for Information | Rectangular Duct Liner | Specification Section 230713-Duct Insulation, section 3.13, paragraphs E,F,G,H,I,J,N,O,P,Q and R all call out for exterior wrap insulation on rectangular duct systems. Specification section 233113-Metal Ducts, paragraph K, section 1 thru 6 call for 1" interior liner on rectangular duct systems. | Please indicate which spec section we are to adhere to for construction and insulation of the rectangular duct systems. | Duct liner shall be provided for rectangular ductwork as directed in specification 233113, section 3.12.K. Medium-pressure supply ductwork, outside air/combustion air ductwork, and any other types not listed in this section shall have external insulation as directed in specification 230713, section 3.13. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 10/30/2019 | Specs 230713 & 233113 |  |  |  | Closed | 11/07/2019 | 11/07/2019 | 11/01/2019 | 10/31/2019 | 10/30/2019
16 |  | 0 |  |  | Request for Information | Temp. Cooling on Roof | On sheet MTC 100.5 is calling out that the temporary cooling units for the Temple as being on the ground. Would it be acceptable to install these units on the existing roof of the Temple? For reference we have attached the submittal showing the weights of the units we are planning on using. |  | While placing the units on the roof would ultimately accomplish getting the air closer to the building, I worry that there could be irreparable structural and architectural implications. Can the existing structure hold the weight of the temporary units? What would the air path be if the units were placed on the roof? Approval would be needed from ARW and CRSA to implement this. Something else to consider is that conditions for the temporary units will fluctuate as construction proceeds. I believe it would be easier to switch out heating & cooling units as needed from the ground rather than bringing in a large crane to lift things up to the roof. ¦ The ability of the structure to support the weight of the temporary units depends on the quantity of units and locations of the units. Please provide a plan showing where the units are intended to be located. ¦ Please update response ¦ After reviewing with the Structural and Mechanical engineers, Putting the Units on the roof will be adding a tremendous amount of additional weight to the Historic Building. We also want to stay away from any additional roof penetration and special mounting of the units that may be required to the existing roof. We have concluded that the units on the roof will not be acceptable. Please proceed with the original intent of the drawings showing the units on the ground. ¦ ¦ ARW please provide a response to the following question posed by the Mechanical Engineer. “Can the existing structure hold the weight of the temporary units?” |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/06/2019 |  |  |  |  | Closed | 11/02/2019 | 11/07/2019 | 11/06/2019 | 10/31/2019 | 10/31/2019
17 |  | 0 |  | AE502, C. 13 | Request for Information | Placement of Filter Fabric | On sheet AE502 it shows Filter fabric surrounding the gravel providing the perimeter drain for the building. In contrast on sheet C.13 it is showing it only on the top of the perimeter drain gravel. Please advise. We have included the effected drawings for your reference. |  | We have consulted with Wayne Rogers with AGEC and he advised that the Filter Fabric at the top of the gravel is sufficient. Please install per AGEC's recommendations. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/31/2019 |  |  |  |  | Closed | 11/02/2019 | 10/31/2019 | 10/31/2019 |  | 10/31/2019
18 |  | 0 |  |  | Request for Information | Temporary Conditioning Requirements | On the MTC and MTH sheets note 1 calls for the Temp. to be 72 degrees +- 10 with 20% to 50% humidity. We have concerns that because of the Width of the conditioning requirements there will be some expansion and contraction in the building that will affect the millwork. For your reference we have included a copy of the Note in question. Please advise or confirm these are required. |  | We realize that is a wide margin to work in. Ideally it would be tighter but during construction it needs to be understood that it will be difficult to maintain a tighter window of operation. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 11/05/2019 |  |  |  |  | Closed | 11/08/2019 | 11/08/2019 | 11/08/2019 | 11/05/2019 | 11/05/2019
19 |  | 0 | 220000 | P503 | Request for Information | P503 IS-1 Fixture | Drawing P503, detail 1 indicates fixture IS-1, instruction room sink is to be procured through Tiffany Marble as indicated. U.S. Mechanical and our plumbing fixture vendor has reached out to Tiffany Marble and been made aware that this particular business does not appear to be in operation any longer. Please provide an alternate vendor/source to procure the IS-1 instruction room sink fixture. | Please provide information for an alternate source to procure the IS-1 fixture. | With this new information, the Owner's Interior Design Team and Gloria Hayley Interiors is going to take a second look and re-design these sinks. New drawings will be developed and released at a future date. |  |  | Low | Justun Bylund | US Mechanical LLC | Interior Designer |  | 12/05/2019 |  |  |  |  | Closed | 02/29/2020 | 04/09/2020 | 11/21/2019 | 12/16/2019 | 11/06/2019
20 |  | 0 |  |  | Request for Information | Equipment on Floors | Due to the height of the ceilings on some of the levels the question has arisen regarding using lifts on the respective floors. If this is a possibility, please advise as to the floors lifts can be used on along with the areas capable of sustaining the loads imposed by the lift along with the weight of the material being lifted. |  | No lifts are allowed on the wood floors of the historic temple unless they are very small single man lifts similar to what is currently used in those areas for periodic maintenance. Lifts are a possibility to be used on the annex floor, but these will also need to be kept to one or two man lifts depending on weight. Please provide design team with the size, weights and configurations of the lifts that are desired to be used for further review and comment. ¦ ¦ Please revise the response to the RFI. thanks |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 11/06/2019 |  |  |  |  | Closed | 11/09/2019 | 11/12/2019 | 11/08/2019 | 11/07/2019 | 11/06/2019
21 |  | 0 |  | AD105, AE105 | Request for Information | Room 515 Raised Floor | On Sheet AD105 note 2.31 is calling for the “EXISTING STAIRS/RAMPS, LANDINGS & RAILINGS TO BE DEMOLISHED & REMOVED”, but it doesn’t mention the raised floor in room 515. Please advise if the landing is to include the raised floor in room 515? For reference we have attached Sheets AD105 and AE105. It appears on Sheet AE105 room 515 does not have a raised floor. |  | Raised Floor is to be demolished with the stairs and landing. Floor in the new Electrical room will be at the same elevation as the rest of Level 5 |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/06/2019 |  |  |  |  | Closed | 11/09/2019 | 11/07/2019 | 11/07/2019 |  | 11/06/2019
22 |  | 0 |  |  | Request for Information | Decorative Counter Brackets | Are the decorative counter brackets a cast or regular steel? |  | These brackets will either be painted steel or stainless steel. The intent is for the brackets to match in color to the Stainless Plumbing Fixtures within these restrooms. |  |  | Low | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/07/2019 |  |  |  |  | Closed | 11/14/2019 | 11/07/2019 | 11/07/2019 |  | 11/07/2019
24 |  | 0 |  |  | Request for Information | Precast notches | 1. In the structural drawings the precast wall between A5.5 and A6.5 along grid AH callout for the top of the precast to be notched for the roof joist to sit in (ref: attached precast elevation H/PC2.01).We suggest making the wall top at the roof joist bearing elevation with a continues embed for welding the joist. The gap between the joists can filled with a 2-1/2” tube steel welded to the embed and deck. This will be a cleaner look. Is this acceptable? |  | Here you go! ¦ |  |  | Medium | Brent Klopfer | Forterra Structural Precast | Structural Engineers |  | 11/13/2019 |  |  |  |  | Closed | 11/16/2019 | 12/05/2019 | 12/03/2019 | 12/02/2019 | 11/13/2019
25 |  | 0 |  | AE180B | Request for Information | Shelves in Storage Rooms | On sheet AE180B there are unmarked rooms adjacent to Rooms 060 and 065 that are empty rooms see attached. Is this room meant to be for storage? If so, should shelves be installed in these rooms. |  | Shelving in these closets will be determined by owner at a later date. ¦ See comments ¦ Shelves are not to be added in this space. ¦ Please provide a resolution to the answer above ¦ Please provide a resolution. |  |  | Low | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/18/2019 |  |  | 250.00 | 1000.00 | Closed | 11/25/2019 | 12/05/2019 | 12/05/2019 |  | 11/18/2019
26 |  | 0 |  | S244 | Request for Information | Contouring Floor Support | On Sheet S244 Detail 13 it shows a new LVL bridging the gap between the high points on a contouring beam this would result in the leveling of the floor. It is out understanding that the floor contouring is one of the items the owner wants to keep. If this is the case, please show the new LVL at the bottom of the contouring beam as indicated in the attachment. | Show new LVL level with the top of the contouring beam. | Detail 13/S244 is specific to Room 518 as seen in Note on S105 (Center Room of East Tower - Between Grids HA-HB & H2.4-H3.6). It is the intent as drawn to level this floor as we are changing the programmatic use from a Locker room to an Instructional Study room and this particular space has too great of sage. The ceiling of Level 4 (assumed to be attached to underside of sagging floor joists) is to remain in place and be preserved and protected, so all of the upgrades are to come from through the floor at Level 5. PDF attachment was a blank page so no additional information was added. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/19/2019 |  |  |  |  | Closed | 11/21/2019 | 11/20/2019 | 11/19/2019 |  | 11/19/2019
27 |  | 0 |  | EY101A | Request for Information | Fire Alarm System, Door Holder release | The gate on level one as indicated by the note on EY101A states a door mag. Do we know if the fire alarm is to control the release of the door mag upon a fire alarm signal? |  | Yes the magnetic hold open needs to be connected to the fire alarm system. The gate is to keep people from continuing down to the basement and to direct them to the nearest exit egress path. |  |  | Medium | Buck Wilkinson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/19/2019 |  |  | 808.00 |  | Closed | 11/22/2019 | 11/21/2019 | 11/21/2019 |  | 11/19/2019
28 |  | 0 |  | AE164, AE662 | Request for Information | Assembly Room Floor Finish | On Sheets AE164 and AE662 it is calling for the floor finish “TBD Custom Color”. Please provide a resolution regarding the method of removing the existing lead infused finish and what the material is to be installed in its place. Eagle Environmental currently has 50 people on-site and are trying to schedule sequencing for them. We are looking to install scaffolding to abate the ceiling. We would like to have resolution on this before they reduce their onsite manpower. Please provide direction regarding floor abatement process and treatment (e.g.; inferred, Chemical or Piranha). |  | Please refer to CCD #3. Please consult with the owner regarding the scaffolding. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/20/2019 |  |  | 20000.00 |  | Closed | 11/25/2019 | 12/19/2019 | 12/04/2019 |  | 11/20/2019
29 |  | 0 | 054000 & 092217 |  | Request for Information | Engineered Metal Stud Shop Drawings | The following spec sections require engineered shop drawings for metal stud framing as follows: SECTION 054000 - COLD-FORMED METAL FRAMING SECTION 092217 – INTERIOR METAL FRAMING The structural drawings include very comprehensive details for both interior and exterior framing. Do you want us to replicate the design for what was already clearly designed in the contract documents or can the requirement for shop drawings be eliminated? |  | The shop drawings do not need to be prepared and stamped by a professional engineer. However, shop drawings are still required for review as noted in the specifications. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/21/2019 |  |  |  |  | Closed | 11/29/2019 | 11/21/2019 | 11/21/2019 |  | 11/21/2019
30 |  | 0 | 221316 |  | Request for Information | Epoxy Coated Cast Iron Pipe | Specification Section 221316, part 2, paragraph 2.2 B indicates cast iron waste and vent piping to be epoxy coated. 2.2 C indicates approved manufacturers as AB&I, Charlotte Pipe and Tyler Pipe. We have inquired of all three piping manufacturers and none of these currently manufacturer epoxy coated cast iron pipe. The only manufacturer that currently offers epoxy coated cast iron pipe in the U.S. market is NewAge. The pipe is manufactured overseas and then distributed domestically thru NewAge. Please confirm that this piping manufacturer is an approved source. | Approve NewAge manufacturing as an approved source of epoxy coated cast iron piping. If not approved, please provide an alternate manufacturer or piping specification for waste and vent piping. | Epoxy-coated cast iron pipe is approved for use on the St George Temple Renovation project. ¦ CRSA defers to VBFA for answer. |  |  | Low | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/27/2019 |  |  |  |  | Closed | 12/06/2019 | 12/19/2019 | 12/17/2019 | 12/02/2019 | 11/27/2019
31 |  | 0 |  |  | Request for Information | Precast base elevation | 1. On sheet S101A the clouded section shown the bottom of panels set at 100'-0". On the Architectural precast drawings sheet AP202 panel Q, the bottom of panel is shown at 1'-6" below 100'-0". Please advice which way to go? |  | Please see ASI #4. Thanks. |  |  | Medium | Brent Klopfer | Forterra Structural Precast | Westland PE’s |  | 12/03/2019 |  |  |  |  | Closed | 12/10/2019 | 12/19/2019 |  | 12/18/2019 | 12/03/2019
32 |  | 0 |  |  | Request for Information | Level 0.5 Room to be Demolished | Please confirm that per a conversation on site between David Adams and Scott Gilberg that the room shown in yellow in the attachment is to be demolished. |  | Room at Level 0.5 are to be Demolished. Please refer to revised ASI #3. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/17/2019 | 12/12/2019 |  | 12/06/2019
33 |  | 0 |  |  | Request for Information | Elevation 100 | Malcolm drilling would like to verify what civil elevation is equal to ARCH 100. We assume from cross-referencing the drawings that ARCH 100 = CIVIL 2681.57. Finish floor on page C.7 varies from 2681.57 to 2681.46. However, page 7 of the geotechnical report indicates ARCH 82 = Civil 2663.57, which is consistent with ARCH 100 = Civil 2681.57. Please confirm ARCH 100 = CIVIL 2681.57 |  | Per conversation with Paul Mogle from Horrocks Engineering, Civil FF elevation 2681.57 is correct and equal to Arch 100 FF. Please disregard the FF 2681.46. |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Westland PE’s |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/12/2019 |  | 12/11/2019 | 12/06/2019
34 |  | 0 |  |  | Request for Information | Micropile Layout | We recently received CCD #002 which updated the micropile layout. Some of the micropile installation will still conflict with the existing structure. Attached is a drawing with proposed modifications for micropile locations. Please review and comment as necessary. |  | ¦ The proposed modifications are acceptable. ARW Engineers takes no exception to what is shown. ¦ See response from ARW stating, "No Exceptions to what is shown". |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Westland PE’s |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/12/2019 |  | 12/11/2019 | 12/06/2019
35 |  | 0 |  |  | Request for Information | Micropile Location | We recently received CCD #002 which modified micropile locations. There are still micropiles that conflict with the existing structure. Attached is a sketch of proposed modification for micropile locations. Please review and comment as necessary. |  | ¦ The proposed micropile locations are acceptable. ¦ Please see Response below from Zach Hansen (ARW). |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Westland PE’s |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/12/2019 |  | 12/11/2019 | 12/06/2019
36 |  | 0 |  |  | Request for Information | MIcropile All-Thread Bar Corrosion Protection | Specification 316330 - Drilled Micropiles Section 2.1 Our micropile designer is recommending Epoxy Coated Grade 75 All Thread Bar in the micropile design. Some of the language in section 2.1 of the specification appears to call for additional encapsulation of the all thread bar. The current design recommendations require epoxy coating of all thread bar and couplers. No encapsulation is required. Please confirm this is acceptable. |  | ¦ Epoxy coated bars and couplers are acceptable. ARW takes no exception to this design recommendation. ¦ See Response from ARW. |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Westland PE’s |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/12/2019 |  | 12/11/2019 | 12/06/2019
37 |  | 0 |  |  | Request for Information | Micropile Drill Pad Elevation | Following previous coordination on site and our understanding of CCD #002, Malcolm Drilling understands that the micropiles will no longer be drilled following interior/exterior excavation activities. It is our understanding, the design team would prefer to have micropiles installed prior to removing soils surrounding the existing stone foundation columns and walls both inside and outside. Sacrificial casing and bar will be incorporated into CCD #002 pricing to accommodate this. Drill pad outside the building is assumed to be approximately EL 98 = 2679.57. Drill pad inside the building is assumed to be approximately EL 93 = 2674.57. Top of micropile is assumed to be at approximately EL 85 = 2666.57. These elevations will need to be confirmed for final micropile design submittal. |  | Please review. Thanks. ¦ Grade elevations for which the drill rig will sit are outside the scope of ARW and will need to be confirmed and coordinated by the General Contractor and the Civil Engineer. The purpose for installing micropiles prior to excavation is to allow the micro pile to be installed as closely to the foundation wall as possible since the stone foundation walls flare at the base. The top of micropile elevation appears to be appropriate if the grades noted are correct. ¦ |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | Westland PE’s |  | 12/06/2019 |  |  |  |  | Closed | 12/13/2019 | 12/12/2019 |  | 12/12/2019 | 12/06/2019
38 |  | 0 | 221429 | P099A, P502 | Request for Information | Sump Pumps under Historic | Plumbing Drawing P099A, plumbing underground at historic, two sumps are shown, one serving the baptismal area drainage and the other located at the east side serving the dewatering system. Drawing P502 details these sumps at both detail 2 and 3 respectively. These details appear to indicate that these sumps are to be pre-manufactured with an epoxy lining. No plumbing specification appears to indicate otherwise. Due to the difficult nature of installing pre-manufactured concrete sumps in the historic basement, please provide alternative methods or manufactured sumps. | Please advise if a poly/plastic or fiberglass sump would be approved for installation at these locations. These sump units are lightweight and durable. | While fiberglass or a poly/plastic sumps are lightweight and durable, they bring concern regarding hydrostatic pressures. If these options were to be utilized, engineering information would need to be provided that 1) detail how the sumps would connect to the mat slab and 2) how the sump walls would resist the hydrostatic pressures. The preferred option would be to keep the pre-manufactured sumps with epoxy coatings. Brian Oswald, VBFA 20-Dec-2019 ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | Mechanical Engineers |  | 12/09/2019 |  |  |  |  | Closed | 12/16/2019 | 12/20/2019 | 12/20/2019 | 12/11/2019 | 12/09/2019
39 |  | 0 |  |  | Request for Information | Beam Penetrations | Assumption is that these pipes extend through the channel. If so, is there a weld requirement? Also, if extension is required, how far? |  | See response from ARW ¦ ¦ The pipes do extend through the channel a minimum of 2” and then are to be welded to the channel with a 5/16” fillet weld all around. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 12/10/2019 |  |  |  |  | Closed | 12/17/2019 | 12/19/2019 | 12/13/2019 | 12/13/2019 | 12/10/2019
40 |  | 0 |  |  | Request for Information | Offsite Storm MH 29 (Sheet C.4) Location does not match CCD | The location of SDMH #29 on the approved offsite drawings (sheet c.4) does not match the conformed onsite drawings tie in called out on sheet C.8. The approved offsite SDMH #29 is already in process of being made. Will an additional manhole be needed for this tie in shown on C.8? See attached snips. |  | There was a revision to the off-site plans. It was approved by the City. This manhole was added in the revision. See the attachment. ¦ |  |  | High | Clint Foster | Sunroc Corporation | Civil Engineers |  | 12/10/2019 |  |  |  |  | Closed | 12/13/2019 | 12/18/2019 | 12/13/2019 | 12/11/2019 | 12/10/2019
41 |  | 0 | 221116 |  | Request for Information | Domestic Water Piping System - Joining Method | Domestic Water Piping, paragraph 2.2, 2.3 and 3.3 indicate the use of solder joint fittings for all domestic water piping systems. This method of joining copper joints will require that hot work be performed throughout the historic structure. Knowing that this building in particular is a fire risk, we propose the following means of joining copper pipe 4" and smaller. | Allow use of press joint systems such as Viega ProPress or similar mechanical joint. No additional cost to install. | Press joint systems such as Viega ProPress or similar mechanical joints are acceptable for use with the domestic water systems inside the historic temple. ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | Mechanical Engineers |  | 12/10/2019 |  |  |  |  | Closed | 12/17/2019 | 12/20/2019 | 12/19/2019 | 12/11/2019 | 12/10/2019
42 |  | 0 | 230000 | M101A | Request for Information | Fire Smoke Damper Clarification | Drawing M101A, between gridlines HA and HB, north and south sprial staircases, reference duct exiting the center of these staircases. No fire smoke dampers are shown like unto other floors at the staircase locations. Please confirm if FSD's are required at these locations. | Confirm whether FSD's are required at the level 1 staircase locations | Provide FSD's for these locations. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Mechanical Engineers |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/31/2019 | 12/30/2019 | 12/13/2019 | 12/13/2019
43 |  | 0 | 230000 | M100 | Request for Information | EF-0-03 & PVC Duct - Dimensions and Elevations | Drawing M100, grid line AH and A7, indicating new exhaust fan EF-0-03 and PVC duct per sheet note 5. No dimensions are shown for the PVC duct and elevations for the fan and duct located within the sewer ejector room 003. | Please provide PVC duct dimensions and exhaust fan and duct elevations within room 003. | The PVC duct should be 8"Ø. The bottom of the duct is at 7'-0" above the basement finished floor. Please see the attached pdf "RFI_43_EF-0-03 & PVC Duct - Dimensions and Elevations_VBFA". ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | Mechanical Engineers |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/20/2019 | 12/19/2019 | 12/13/2019 | 12/13/2019
44 |  | 0 | 230000 | M100A | Request for Information | Another Fire Smoke Damper Clarification | Drawing M100A, at gridlines HE, HC, H2 and H4 there are approximately 10 riser ducts that do not have fire smoke dampers shown like unto the other shaft riser ducts in close proximity to these locations. | Please confirm if the duct risers shown without FSDs are correct or if they are to have FSD's as well. | See VBFA's response ¦ Brian Oswald (VBFA INC CONSULTING ENGINEERS) FSD's are to be provided for duct risers that serve levels 2 or 3 (Mezzanine). FSD's are not required for duct risers that only serve the baptistry floor. (2) Tags for FSD's were found to be missing and were added to sheet M100A. Refer to RFI 53 for the revised sheet. Brian Oswald, VBFA 31-Dec-2019 |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 01/02/2020 | 01/02/2020 | 12/31/2019 | 12/13/2019
45 |  | 1 | 230000 | M101A | Request for Information | RM 064 Supply Grilles | Drawing M101A, gridline H4 between gridline HA and HB at room 064, two supply grilles are shown. No type/size and CFM requirement are shown. (The RFI is referencing the supply air registers at the ceiling, not the return air grilles at the floor. Please advise.) | Please provide type, size and CFM requirement for these grilles. | The supply diffusers for Confirmation 063 and Confirmation 064 are all type CD-3 with 8"Ø connection and balance to 170 CFM. See sheet M100B for reference. Brian Oswald, VBFA 30-Dec-2019 ¦ Sorry, my mistake I am having a Friday brain today..... Brian - are the SUPPLY the same as room 063 as well? 8" Diameter CD-3, (2) 170? |  |  | Medium | Camron Walker | Westland Construction, Inc. | Mechanical Engineers |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/31/2019 | 12/30/2019 | 12/13/2019 | 12/13/2019
46 |  | 0 | 230000 | M106 & M101 | Request for Information | Intake Hood IH-3 Clarification | Drawing M106, gridline AH between gridline A4 and A5 is shown intake hood IH-3. Drawing M101, same gridline location does not indicate any duct or airside equipment to be served by intake hood IH-3. | Please provide direction as to what system/equipment intake hood IH-3 is to serve. | See attached ¦ See updated response to Intake Hood IH-3 ¦ ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 01/10/2020 | 01/08/2020 | 01/07/2020 | 01/06/2020 | 12/13/2019
47 |  | 0 | 230000 | M603 | Request for Information | SRW-1 Grille Schedule | Drawing M603, diffuser, register and grille schedule reference two separate SWR-1 grilles. The ID, Manufacturer, Max NC, Image and Description all appear to be the same. The quantities are not the same (181 vs 2). | Please Provide additional information on both SWR-1 grille items indicating the differences between the two. | See attached |  |  | Medium | Westland PE’s |  | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/31/2019 | 12/31/2019 | 12/30/2019 | 12/13/2019
48 |  | 0 | 237313 | M Sheets | Request for Information | AHU-3 Fan HP Change | Per VBFA response to the approved AHU submittals, please verify that the current power selection for the return/relief fans for AHU-3 is acceptable. The fan horsepower selection was changed from 2hp on the original schedule to 2.5hp in order to meet the design demand. See approved submittal pages 54 and 63 for reference. | Confirm hp change is noted by electrical engineer. | Confirmed that HP change on AHU-3 Return fan going from 2HP to 2.5HP motors does not impact wire or breaker sizes for electrical connection to unit. Scott Hardy, Envision Engineering ¦ |  |  | Medium | Westland PE’s |  | Mechanical Engineers |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/30/2019 | 12/19/2019 | 12/16/2019 | 12/13/2019
49 |  | 0 |  |  | Request for Information | Branch Circuit Conduit Paths | Can we route branch circuit conduits in the concrete deck between basement and level 1 we would need less space above the ceilings for conduit racks if we could route encased in concrete deck? |  | Conduit is not allowed to be placed inside the concrete slab on deck. Please run any conduit racks etc. below the concrete floor deck. ¦ No. See comment from Zach Hansen (ARW ENGINEERS) ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 12/20/2019 | 01/03/2020 | 12/20/2019 | 12/16/2019 | 12/13/2019
50 |  | 0 |  | AE383 AE384 GA005 | Request for Information | Wood Flooring Thickness | Stair 3 Floor Finish denotes Hardwood Flooring at Landings and Hardwood Stair Treads (ref: sheets AE383 & AE384). GSW has been unsuccessful in locating anywhere that provides thicknesses to be used for this wood material. Sheet GA005 refers us to finish schedules on AE660, AE661, AE662 - but there is no dimension provided. In the past we have seen this dimension vary from 1.5" to 2.25". Please provide if possible - this affects our ability to detail the stair. This also applies to the other stairs - if possible please provide information for them as well. |  | Westland & sub are currently sourcing the wood flooring from Carlisle, no spec is nailed down yet. See Sheets AE510 - Stair Details, the design intent is for the stained wood treads to be 1-1/4" thick with a 5/8" trim below. Wood treads shall not exceed 1-1/2" thick. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 01/09/2020 | 01/08/2020 |  | 12/13/2019
51 |  | 0 |  | AE383 through AE387 | Request for Information | Stair 3 Elevations | Elevations (Top of Floor & Top of mid Landings) Do not match between plan views and elevation views. The differences range from 1/8" to 1/4". Please clarify which dimensions we are to follow. |  | In general the elevations noted on Plan View are accurate. Sheets AE383 - AE387 have been updated and are attached. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/19/2019 | 12/18/2019 |  | 12/13/2019
52 |  | 0 |  | AE383 Through AE387 | Request for Information | Stair 3 Level 2 to Mid Landing | The Stair run from Level 2 (elevation 111'-6-1/2") to the mid landing at elevation 118'-1-1/2" is called out on the drawings as needing 10 treads. If this amount of treads occur - this will place the riser heights at 7-3/16". Sheet AE511 denotes a maximum riser height of 7". Please clarify. |  | Note of 10 Treads is incorrect, there should be 11 Treads. See Detail A4/AE387 which correctly shows 11 Treads and 12 Risers between Level 02 and Landing 03. We should be closer to 6-1/2" risers across this flight of stairs. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/19/2019 | 12/13/2019 |  | 12/13/2019
53 |  | 0 | 230000 | M100A | Request for Information | RM 043 Supply Air Duct | Drawing M100A, mechanical room 043 at gridline HH and H5 are two supply air duct penetrations at the mechanical room 1 hour rated walls. No indication of fire smoke damper is shown on these supply duct penetrations. One is shown on the return duct penetration. See attached snapshot. | Please clarify if fire smoke dampers are required on these two supply duct penetrations. | See Attached ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 01/02/2020 | 01/02/2020 | 12/31/2019 | 12/13/2019
54 |  | 0 |  | 55/GA003 | Request for Information | Wall Type 55 - WP 1570 | Plans show 5/8" drywall on both sides of 6" studs. CCD #1 added note for wall to be similar to WP 1570. This GA file shows 3/4" type x drywall on both sides. Please advise if we are to install 5/8" gypsum board or 3/4" gypsum board. |  | 5/8" Gyp. Bd. may be used at walls that are not a part of the fire rated assembly areas. NO substitutions are allowed at Fire Rated portions or areas specified on the code review drawings (GI Sheets). Please refer to ASI #05 for further instruction. |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/20/2019 | 12/30/2019 | 12/23/2019 | 12/13/2019 | 12/13/2019
55 |  | 0 |  | GA003-GA004 | Request for Information | Wall Types - GA file assemblies - Proprietary | CCD #1 added notes to various wall types with the wording "SIMILAR TO GA FILE NO….". Many of the assemblies provided are proprietary and require drywall from specific manufacturers. Please advise if it is acceptable to use alternate products equal to those specified in the GA files. |  | Please see ASI #05. |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 12/13/2019 |  |  |  |  | Closed | 12/23/2019 | 12/30/2019 | 12/23/2019 | 12/16/2019 | 12/13/2019
56 |  | 0 | 321413 |  | Request for Information | Spec 321413.2.1 Questions | The spec section for unit pavers calls for Belgard concrete pavers. The landscape drawings all refer the paving to be Endicott brick pavers. Please confirm paving material. |  | References to Belgard are incorrect, the plan references to Endicott are correct. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 12/16/2019 |  |  |  |  | Closed | 12/23/2019 | 12/30/2019 | 12/19/2019 | 12/17/2019 | 12/16/2019
57 |  | 0 | 230000 | M100 | Request for Information | Open Pit 034 Louvers | Drawing M100, gridlines AH and A4 at open pit 034, one new louver and two existing louvers are shown installed within a rated wall. No fire smoke dampers are shown. See attached screenshot. | Please advise if FSD's are required at these louver locations. | See VBFA's response ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/16/2019 |  |  |  |  | Closed | 12/23/2019 | 01/02/2020 | 01/02/2020 | 12/31/2019 | 12/16/2019
58 |  | 0 | 230000 | M100B, M102, M103 & M101A | Request for Information | FSDs Locations at Stair Towers | Drawings M100B, M101A, M102 and M103 at gridlines HA to HB, fire smoke dampers (FSDs) are indicated to be installed at both the north and south sprial stair towers. The locations shown do not appear to match the rated assemblies shown on the code drawings (GI). Detail 1/M402 does not provide additional FSD location info. See attached snapshot for clarification. | Please confirm the locations for this FSD's as shown currently are correct. | See VBFA's response ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/16/2019 |  |  |  |  | Closed | 12/23/2019 | 01/02/2020 | 01/02/2020 | 12/31/2019 | 12/16/2019
59 |  | 0 |  |  | Request for Information | Circuits on Chandelier Hoists | How many circuits (and or wires) are needed for each light fixture having a chandelier hoist? How heavy is each chandelier? (will any require a 2000 lb hoist or will a 1250 lb hoist be sufficient for all chandeliers?) | These typically do not run any emergency light backup system in these light fixtures. This would cause a larger than normal size cable. | Hi Dan, I'll send over the estimated weights and circuits before the weekend. -Please provide a schematic of your lift attachment. -Please confirm which of the following fixtures require a lift that you'll be providing: -Celestial Room Large Chandelier 84"x150"L Qty. (1) -Celestial Room Side Pendants 30"x65"L Qty. (4) -Large Sealing Room Chandelier Type 1 72"x132"L Qty. (1) -Medium Sealing Room Type 2 Room #148 60"x65"L Qty. (1) -Small Sealing Room Type 3 Room #216 48"x82"L Qty. (1) Are there any others in Family B, C, or D? Thank you, Claudia |  |  | Low | Dan Lopez | Drive Motorlifts, L.L.C. | Claudia Hawkins | Swarovski Lighting Ltd. | 12/19/2019 |  |  |  |  | Closed | 12/31/2019 | 01/09/2020 | 01/02/2020 |  | 12/16/2019
60 |  | 0 |  | P201 | Request for Information | Roof Drains in Spiral Stair Case | On sheet P201 it is calling for use to notch the Center of the spiral staircase support walls for a 4” roof drain. Our concern is that wen we start to notch the stone out that the stone may brake lose on the other sided and cause significant aesthetic impacts to the towers? | Should a we surface mount the pipe and build a false wall be built to hid it? | After reviewing with the structural Engineer and the drawings, the stone in the areas that are being notched is over 3' thick and is not a concern. There is an upcoming CCD #12 that will give more instruction and to clarify. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/19/2019 |  |  | 1500.00 | 1500.00 | Closed | 12/23/2019 | 01/29/2020 | 01/27/2020 |  | 12/16/2019
61 |  | 0 | 230000 | M100A | Request for Information | Return Duct Dimension at Grid HG | Drawing M100A, gridline HG and H4, return ductwork branch running south along gridline HG is missing a dimension directly following the FSD and before the transition shown. See attached clouded duct for reference. | Please provide dimension of the clouded return ductwork. | See attached from VBFA ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/16/2019 |  |  |  |  | Closed | 12/23/2019 | 12/31/2019 | 12/31/2019 | 12/30/2019 | 12/16/2019
62 |  | 0 |  |  | Request for Information | Deco Lighting Family B Arm Question | Please see the attached question about the metal arm on Family B. Do you want Option A or B used on this family? -Option A the simplified arm as shown in the concept images? -Option B the more decorative arm with the key, etc.? Family B: Proxy Sealing 3rd Floor SR #318 |  | This question was resolved in the deco lighting design meeting. ¦ |  |  | Medium | Claudia Hawkins | Swarovski Lighting Ltd. | Interior Designer |  | 12/16/2019 |  |  |  |  | Closed | 12/23/2019 | 08/20/2020 | 08/20/2020 | 12/16/2019 | 12/16/2019
63 |  | 0 |  |  | Request for Information | Elevator Ceilings | The bid documents specified the ceilings to be “medium oxidized bronze lacquered to match front wall”. However in the conformance drawings these ceilings are shown to be painted gyp. ceilings. As such, the elevator manufacturer has removed ceilings and lighting from his pricing, and is expecting the drywall sub and millworker to provide the ceilings with the electrician providing the lighting. The lighting, however, is not called out. Please provide information for the lighting in the elevators 2 through 5. As a side note, the escape hatch shown in the elevator RCPs will not work. Coordination between the Otis, the electrician, the millworker, and the drywaller will need to be performed to ensure the hatch is accessible. | Please provide information for the lighting in the elevators 2 through 5. | The response to this RFI is part of an upcoming CCD-57. |  |  | Medium | Hyrum Ence | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/18/2019 |  |  |  |  | Closed | 12/27/2019 | 06/09/2020 | 05/18/2020 |  | 12/18/2019
64 |  | 0 |  |  | Request for Information | Window Stool Demo | Please confirm that per a phone conversation between David Adams and Kyle Welch that the stool and around the perimeter of the window is to be Demoed. This will allow for the Window to be removed when it is time. |  | Wood trim, Tile or portions of plaster splays at interior sills along window frame may be removed for window replacement. Provide reference documentation of existing condition of each window before demo. This will be used during the new construction and rebuilding the new window plaster splays and bevels etc. GC is to set up a meeting with Architect and Demo Contractor to walk through and review methods of removal before window demo starts. See attached photos for reference from earlier window replacement/ study. |  |  | Medium | Travis Keenan | TID, Inc. | CRSA ARCHITECTURE |  | 12/19/2019 |  |  |  |  | Closed | 12/24/2019 | 12/31/2019 | 12/23/2019 |  | 12/19/2019
65 |  | 0 |  | LP101, LP108A & LX101 | Request for Information | Tree Removal Clarification | This tree (see attached) is shown on the tree demo plan, but appears to be still on the planting plan. Is this tree to be removed? Please advise. |  | As noted on redlined RFI 65 Snips.pdf exhibit, do not remove this tree at this time. There remains discussion between CRSA, the Church Landscape Architect, and Church Project Management on the status of the tree in question. Further discussion will be required. Thank you ¦ |  |  | Medium | Westland PE’s |  | Landscape Architects |  | 12/19/2019 |  |  |  |  | Closed | 12/26/2019 | 12/30/2019 | 12/26/2019 | 12/20/2019 | 12/19/2019
66 |  | 0 | 057000 | AE525 | Request for Information | Baptistry Font Attachment to Foundation | When removing the historic font, the attachment of the bottom pan to the side walls was discovered. It is evident that historically the font was assembled completely then lowered in place on a bed of mortar, covering the bolted attachment. Since lifting the entire font for re-installation isn't practical with the space and means we have now, it is desirable to create an attachment that leaves the bolted connection exposed. The question is: Can the foundation detail be changed to allow an exposed bolted connection? | I have created a sketch of the detail we propose along with the current detail from the architectural sheet AE525. The new detail would require some additional build out to the finished surface. For our part it would be a no cost change. | ARW does not have issues with reworking this connection in a manner similar to what is proposed. We agree that more dimensional information may be needed in order to determine if the proposed connection will work. A couple of considerations are: 1) Will the connection plate on the exterior of the wall interfere with attachment of the oxen. 2) Are the existing threaded holes in the font in a condition to be reused and is that connection strong enough to secure the font? ¦ No issues have been presented in altering the foundation as proposed. This item is continuing to be developed and coordinated between CRSA, ARW, & HACI ¦ |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 12/23/2019 |  |  |  |  | Closed | 01/24/2020 | 01/30/2020 | 01/16/2020 | 12/30/2019 | 12/23/2019
67 |  | 0 | 057300 | AE524 | Request for Information | Reproduction of Historic Elements of the Babtistry Rails | Given the samples of the historic Parts we have, how much refinement should we do to improve or eliminate the existing flaws? I have attached images with notes of the type of irregularities we are seeing. In the historic rail many of the foundry flaws were covered or minimized with fill and paint. The more pertinent question is with the irregularity of the original tooling. We see variation in the fluting in particular. Also, the clean up of the parting lines. Some of the shapes of the molding profiles are also irregular. | Many of the flaws come from problems they had in the foundry process, the porosity in particular. Those should be eliminated as the base material of the new rail will be exposed. Regarding the irregularities in the tooling. We feel that the design features should be improved as the flaws will be more noticeable with the refined bronze finish. | During a couple of site visits to Historical Arts & Casting, it has been discussed to fix casting issues seen in the pitting and seams, but to leave the irregularities in flute size to give it a more hand made appearance. |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 12/24/2019 |  |  |  |  | Closed | 01/06/2020 | 01/25/2020 | 01/16/2020 | 12/30/2019 | 12/24/2019
68 |  | 0 | 057000 | AE524 | Request for Information | Baptistery Oxen Mounting | This is a multi part question: Are the oxen to be mounted in a way to plan for embedding their feet in the floor? Are the oxen to be mounted in a way to plan for their bodies to be embedded in the in wall below the font? The architectural drawing shows oxen that are 3'-5" tall. The drawing also shows it on top of the tiled surfaces. The oxen are actually 3'-8" tall. In order to allow for the 1 3/4" reveal above the oxen, an adjustment would need to be made to either their height, their embedment or the elevation of the finish floor beneath them. See attached drawing and pictures with my notes regarding these topics. If an adjustment needs to be made to the elevation of the oxen or finished floor anyway, do you want to consider adding hooves onto their legs while we are at it? | Regarding the elevation of the oxen, I would add hooves and adjust the elevation of the finished floor of the moat to achieve the desired reveal above the oxen. Where the oxen meet the wall, I would mount them and then bring the finish tile in around them. | During a couple of site visits to Historical Arts & Casting, this item as been discussed at length. The oxen will be mounted to the framed wall (anchored through the foundation). Options are being discussed with HACI on how to finish the joint between the oxen and the vertical surface. There will not be any hooves added to these oxen, however a standoff with trim will be designed to allow the floor tile to be installed cleanly. |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 12/26/2019 |  |  |  |  | Closed | 01/06/2020 | 01/30/2020 | 01/16/2020 | 12/30/2019 | 12/26/2019
69 |  | 0 |  |  | Request for Information | Tie Rod Cores and Grouting Options | 1) Details 6/S240, 1,3/S242. We submitted RFI 001 requesting the option to sleeve the tie rods at the existing stone walls, pour the jacket walls in place and then install the rods. In reviewing this we would like to propose pouring the jacket walls first as an option and then having the core drill take place after the jacket wall concrete is placed. This would facilitate the core driller with a flat surface to drill against. Please verify if this is an acceptable approach. 2) Please provide the anticipated core size diameter that is planned for the 1" tie rods 3) Would it be acceptable to use epoxy grout around the tie rods or do we need to use epoxy? |  | See ARW's Response ¦ ¦ See below for response: 1) We take no exception to this proposed method. 2) Please provide a core hole that is 1/4" max oversize. 3) Epoxy grout can be used if the viscosity of the grout is such that it will allow adequate penetration to fill voids between stone and tie rods. |  |  | Low | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 12/30/2019 |  |  |  |  | Closed | 01/09/2020 | 01/07/2020 | 01/02/2020 | 01/02/2020 | 12/30/2019
70 |  | 0 |  |  | Request for Information | Epoxy specifications/ missing embedment depths | (EXTRA COSTS COULD BE INCURRED PER THIS RFI) Reference structural notes S001 and attached epoxy dowel summary spreadsheet. 1) Approved epoxy types per structural notes on S001 are Hilti-RE 500V3, Hilti HIT-HY 200, Simpson Set-XP or AT-XP and Dewalt Pure 110+ or AC200+. For locations and details not requiring specific epoxy types we would like to propose Hilti HIT-RE 100 and Hilti HIT-HY 100 as an optional epoxy to be used on the project. Please verify if this is acceptable. 2) Please provide epoxy embedment depth at the following details: 3/S212, 1/S241, Slab embedment details 3/S221 and 13/S220. #3 dowels detail 6/S240, Dowel into stonewall detail 1/S241, 2/S241, Vertical dowel into basalt trench detail 1/S242, 3/S242, Stonewall dowels 1/S243 and basalt trench vertical dowels 1/S243 |  | See ARW's response ¦ ¦ See below for response: 1) Please use the approved epoxy types shown in the structural notes. These epoxy types were chosen based on previous anchor testing in the existing stone. 2) 3/S212 references 1/S241 which specifies 24" embedment in the notes. 3/S221 Please use 8" embedment for dowel into the existing slab. This will be clarified on an upcoming ASI. 13/S220 the U-bar note indicates 19" embedment and the slab dowel dimensions are shown in the note. 6/S240 #3 dowel dimensions are shown in the detail. Embedment depth would be approximately 12". 1/S241 says to use 24" embedment. 2/S241 uses the same embedment depth as 1/S241 but has a typo referencing detail 1/S204 instead of 1/S241. This clarification will be made in an upcoming ASI. Vertical dowel embedment is not required. This clarification will be made in an upcoming ASI. 1/S243 references 1/s242 and 1/S241 which includes a 24" embedment note. Vertical dowel embedment is not required. This clarification will be made in an upcoming ASI. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 12/30/2019 |  |  |  |  | Closed | 01/06/2020 | 01/09/2020 | 01/02/2020 | 01/02/2020 | 12/30/2019
71 |  | 0 |  |  | Request for Information | Annex shear walls, SOG, SOD and structural steel coordinatio | (EXTRA COSTS COULD BE INCURRED PER THIS RFI) Sheet references S100, S101A, detail 8,10/S210, A,B/S301 1) Reference shear walls at grids AD, AE on sheet S100. Please verify if it would be acceptable option to pour a stem wall for these shear walls in lifts from elevation 85'-0" to 87'-0" to allow the backfill and slab on grade to be poured. Vertical wall rebar would be spliced at elevation 87'-0". Reference screen shot of detail 8/S210 on attached sheet S301. 2) Reference mark ups on elevation details A,B/S301. Please verify if acceptable to pour walls on grids AD and AE to FF elevation 100' and then have structural steel to be set at level1 and slab on metal deck poured before topping out the remaining wall lift? With the upper roof trusses tying into the perimeter precast walls we assume this would not be an issue with steel plumb up and provide a safer and better work surface for the upper sections of annex work to be completed. Also based on the details of how the CMU dowels tie into the slab on deck on level 1 at the shafts and stair wells this appears to be the intent of the sequence of construction. |  | See ARW's response ¦ ¦ See below for Response: 1) It will be acceptable to pour the wall to elevation 87'-0". Vertical rebar shall run continuous through the joint at lengths that provide adequate rebar splice lengths per the rebar lap splice schedule. The top of the wall at elevation 87'-0" shall be prepared per the structural notes E.8 and E.9. 2)Construction sequencing is outside the scope of ARW and should be coordinated with the general contractor. If it is desired to provide a construction joint in the wall at elevation 100'-0" we take no issue with that. It will be necessary to provide the joint that meets what is described above in our response to item #1. All detailing of slab to wall and floor beam to wall connections shall remain as shown in the drawings. ¦ Can you take a look at this Jay for the sequencing portion? |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Jay Webster | Westland Construction, Inc. | 12/30/2019 |  |  |  |  | Closed | 01/06/2020 | 01/07/2020 | 01/02/2020 | 01/06/2020 | 12/30/2019
72 |  | 0 |  |  | Request for Information | Mech Access Doors 3rd & 5th Floors | The mechanical access doors on the 3rd and 5th floor have lead paint. The access doors on the 3rd floor are going to be demoed with the wall but we are unsure about the 5th floor. Are the doors show in the attached photo supposed to be demoed on the 5th floor? |  | No attached photo. Yes, all the mechanical access doors on Level 3 & 5 (leading into the ceiling above Level 2 or Attic above Level 4) are to be removed and returned to the Owner. New flush mounted access panels are to be provided. ¦ Yes, the response is still correct. All attic/mechanical access panels on Level 3 & 5 are to be removed and returned to owner. |  |  | Medium | Creg Norton | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/06/2020 |  |  |  |  | Closed | 01/10/2020 | 01/08/2020 | 01/07/2020 |  | 12/30/2019
73 |  | 0 |  |  | Request for Information | 5th Floor Ceiling Demo | The ceilings on level five are called out to be gyp board and to be demoed. They are lath and plaster and not gyp board and would be a additional 13,710 on top of what we had in for the gyp-board ceilings on level five. How do you want us to proceed |  | Please see CCD 11 showing how to proceed. |  |  | Medium | Travis Keenan | TID, Inc. | CRSA ARCHITECTURE |  | 12/30/2019 |  |  |  | 13710.00 | Closed | 01/06/2020 | 01/09/2020 | 01/09/2020 | 12/31/2019 | 12/30/2019
74 |  | 0 |  |  | Request for Information | Precast Elevation from Shop Drawings (Type E vs Type F) | Annex Bldg – PreCast Shop Drawings (dated 10-7-19) – Sheet PC2.02 (S) Precast Elevation – All (4) of the Full Circle openings across the top are noted to have a R1’-6 3/4” (37.50”) opening which is what the Window Type E is designated to have. However the Architectural Elevation drawings on sheet AE204 technically have the (2) inside full circle openings designated as Type F and not Type E as shown on Precast shop drawings. For what its worth I believe they all should be Type E (for a total of 6 openings) but this needs to get clarified. The Type F openings should only be across both sides of the East and West elevations of the Annex. Link to Submittal |  | The windows noted as Type F on AE204 are incorrect. All 6 full circle openings on the North Entrance shall be Type E (matching). |  |  | Medium | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/06/2020 | 01/09/2020 | 01/02/2020 |  | 12/30/2019
75 |  | 0 |  |  | Request for Information | 3 Missing Demensions for FSD's on M100A | Drawing M100A, appears a total of three (3) fire smoke dampers (FSD) are missing dimensions. See attached for reference. | Please provide dimensions for the FSD's indicated on the attached screenshot. | See VBFA's response ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/09/2020 | 01/08/2020 | 01/08/2020 | 12/31/2019
76 |  | 0 | 230000 |  | Request for Information | FSD's on Mechanical vs EY Drawings | The conformed EY drawings appear to have ll fo the fire smoke dampers shown as connected to the fire alarm system panel. Does a FSD matrix exist on the mechanical drawings that matches the EY drawings? | Please provide a fire alarm numbered matrix indicating labeling that matches the fire alarm control panel per the EY drawings. | this RFI is not needed any more. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/31/2019 |  |  |  |  | Closed | 01/24/2020 | 02/21/2020 | 02/21/2020 | 01/02/2020 | 12/31/2019
77 |  | 0 | 220000 | AE251, P106 | Request for Information | Roof Drains at East Tower | Drawing AE 251, detail C4, drawing P 106A indicates roof drains at east tower, near gridlines H3/HA. See attached drawings. Existing roofing material appears to be standing seam fiberglass panels. See attached photos. Note that drawing AE 251 general notes indicate all fiberglass panels to remain. | Please confirm if roof drains are to be installed directly on top of fiberglass panels, beneath panels, or if slope/pitch will be provided to better drain this area. | Omit these Roof Drains. It does not appear that these drains are going to work as drawn. The fiberglass is not structured / sloped to accommodate these drains, therefore they are to be omitted from the project. East tower will continue to drain via existing scupper onto the main roof of the Temple. ¦ Brain, can you confirm if these drains are new adds or just replacement of existing drains. To our recollection, these roofs just sheet flow to the edge. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/14/2020 | 01/13/2020 | 01/08/2020 | 12/31/2019
78 |  | 0 |  |  | Request for Information | AHU-5 Return Duct Elevation Routing at Basement Font Area | Drawing M100A, between gridlines HG to HF are two (2) 36x32 and one (1) 66x36 return ducts routing from the basement font room to AHU-5. Drawing S100A indicates that the floor height of this area where duct is shown to be installed is 88'9" FFE. Drawing AE340, detail 1 indicates the FFE level to be 87'. It appears that the ductwork as shown will need to be routed approximately 2' below concrete slab. See attached for clarification. | Please confirm if the return ductwork shown is to be installed within the soil/dirt or if there is to be a concrete tunnel/chase for install and routing purposes at these locations in the basement. | See CCD 013 that shows the concrete chases. ¦ ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/22/2020 | 01/21/2020 | 01/17/2020 | 12/31/2019
79 |  | 0 |  |  | Request for Information | Added Keypads at Gate and Security Office | Question about Addendum #7 (CRSA Addendum 6). Three keypads were added (two at the gate and one in the security office). What system are we looking to tie these keypads into? Is there an existing access control system or will these be kind of a standalone system that just needs to open the gate and communicate back with the security office? |  | The keypad control system for the west gated entry is intended to be a 'stand-alone' type system for the gate only as there is no other electronic access control system for the temple. The details of the controls for this system will depend on the specific product information for the gated entry and what control/interface options are available for that specific product. Is the submittal for the gated entry available at this point? It is recommend that the contractor review the product options and propose a control system for review that meets the project requirements. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/06/2020 | 01/03/2020 | 01/02/2020 | 12/31/2019
80 |  | 0 | 230000 | M100B | Request for Information | Cooridor 065 Missing FSD | Drawing M100B, corridor 065 appears to be missing a FSD at indicated attached location. | Please clarify if an FSD is required at this location. | Per VBFA, Yes a FSD is required in this location ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/09/2020 | 01/08/2020 | 01/08/2020 | 12/31/2019
81 |  | 0 | 230000 | AD125, M105, MP105 | Request for Information | Level 5 Ceiling Conflict with New HVAC-PLBG Systems | Drawing AD125, key note 2.126 indicates existing ceiling to remain at north and south corridors. Drawing M105 and MP105 indicate new duct, VAV's and mechanical piping to be routed above existing ceilings. Existing ceilings will need to be removed at these locations to allow for installation of mechanical and plumbing systems. See the attached drawings. | Please confirm existing ceilings at these locations will be removed to allow for installation of new mechanical and plumbing systems. | Existing ceilings in the North and South corridors needs to remain. New mechanical and electrical installation shall be accessed through attic space and through the adjacent rooms where the ceiling is being removed. |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/31/2019 |  |  |  |  | Closed | 01/08/2020 | 01/09/2020 | 01/09/2020 |  | 12/31/2019
82 |  | 0 |  |  | Request for Information | Finish Schedule Marble Clarifications | Two Questions: The Finish Schedule AE660 calls out BS1 as M240 Thassos White Marble slab from Daltile. However, the closest material I can find on Daltile’s website is M420 Thassos Snow White marble. Is this the correct material? The Finish Schedule also calls out BT3 as Thassos BQ100P quartz slab from Inside Out Architecturals, but after contacting Inside Out Architecturals for samples, I was told they are not the supplier for this material. Is the BT3 material supposed to be M420 Thassos Snow White marble from Daltile or Thassos BQ100P quartz from Pental Quartz? |  | See GHID response ¦ ¦ We would like to press forward with the Thassos marble for both items and remove the quartz completely. Updated finish plans/legend to follow. |  |  | Medium | Nathan Gheen | GLOBAL STONE & TILE LLC | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 01/10/2020 | 01/30/2020 | 01/27/2020 | 01/24/2020 | 01/03/2020
83 |  | 0 | 230000 | M602, M701, M710, M711 | Request for Information | Missing Fan Coils per equipment schedule | Drawing M602, fan coil schedule indicates a total of eight (8) fan coils to be installed at stairwells 6 and 7 that cannot be found on the mechanical drawings. Drawings M701, M710 and M711 indicate airflow and hydronic piping routing to these fan coils. See attached schedule for clarification. | Please advise if these fan coils are to be installed and if so provide drawing indicating locations. | See VBFA's response ¦ This information will be included in CCD38 to be released shortly. ¦ ¦ ¦ ¦ VBFA, The fan coils are missing on the CCD per my Prior response. Please revise and coordinate with CRSA on a new CCD number. Thanks. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/09/2020 |  |  |  |  | Closed | 01/13/2020 | 03/19/2020 | 03/18/2020 | 03/11/2020 | 01/03/2020
84 |  | 0 | 230000 | M602, M104, MP104 | Request for Information | Level 4 missing fan coils | Drawing M602, fan coil schedule indicates FC-4-04A, 4-04B, 4-05 and 4-06 to be located in rooms 409, 410, and 411. These fan coils are not shown on drawings M104 and MP104. See attached for clarification. | Please confirm these fan coils are to be installed per M602 and provide drawing detail. | See VBFA's response ¦ This information will be included in CCD38 to be released shortly. ¦ ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/09/2020 |  |  |  |  | Closed | 01/13/2020 | 03/19/2020 | 03/18/2020 | 03/11/2020 | 01/03/2020
85 |  | 0 | 230000 | M101 | Request for Information | Room 112 Missing Return Grille | Drawing M101, room 112 is shown a return duct at the south wall with no dimensions given. Drawing AE108, detail C4, note 23.01 call out for a decorative return grille at this location. See attached for clarification. | Please provide a return grille size for this location. | See VBFA's response ¦ ¦ ¦ ¦ This return grille has a 14"x14" duct connection. Brian Oswald, VBFA 08-Jan-2020 |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 01/13/2020 | 01/09/2020 | 01/09/2020 | 01/08/2020 | 01/03/2020
86 |  | 0 | 230000 | CCD#007, M101 | Request for Information | CCD#007-Room 112 | CCD#007, drawing M101, Room 112 appears to indicate two sound boots with missing grille call outs/information. See attached for clarification. | Please clarify if sounds boots are needed as there is already a low return in this space. If so, provide grille size for these sound boots. | See VBFA's response ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 01/13/2020 | 01/09/2020 | 01/08/2020 | 01/08/2020 | 01/03/2020
87 |  | 0 | 230000 | M100A, AE100B, S222 | Request for Information | Fire rated assemblies at M100A | Drawing M100A, between grid lines HE to HC and H2 to H4, there are shown multiple floor installed fire smoke dampers (FSD). Drawing S222 indicates a floor opening assembly at these locations. Detail 9 on this same drawing does not indicate TYPE of rated assembly to be installed. Drawing AE100B, same locations, does not appear to provide any detail on type of rated assembly to install. See attached for clarification. | Please provide type and detail of rated assembly required at these locations. | The floor assembly is Type F1 (Sheet GA005) and has a 1-hour fire rating. Rated floor penetrations must comply with the 1-hour rating seen on Sheet GA006. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/03/2020 |  |  |  |  | Closed | 01/13/2020 | 02/20/2020 | 02/19/2020 | 01/06/2020 | 01/03/2020
88 |  | 0 |  |  | Request for Information | Level 3 Demo Clarifications | We need some clarification on these level 3 demo items: Do we remove the plaster above the acoustical tile in the hall and above the ceiling in the bathrooms and above the tile in the foyer to the stair tower. South hall area arches dashed explain, Arches. North hall area arches dashed area, Arches. Explain also. North and south hall post explain. There is no acoustical in center room of the stair tower. |  | See Comments added. |  |  | Medium | Creg Norton | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/06/2020 |  |  |  |  | Closed | 01/13/2020 | 01/30/2020 | 01/24/2020 |  | 01/06/2020
89 |  | 0 |  |  | Request for Information | Replace Not Relocate Trees From CCD 6 | Please verify that the two trees discussed in CCD 6 are now to be removed and destroyed and not relocated. Please provide species and caliper for the trees to be placed in the locations shown on LX101 per CCD 6. | Eric said CRSA recommended: Species: Ulmus parvifolia ‘True Green’ (True Green Elm) Size: 6-8” caliper | Correct, the two trees identified in CCD 6 are to be removed and replaced with 7" caliper Ulmus parvifolia 'True Green' (True Green Elm) See attached LX101 to see the location for the replacement trees highlighted in red. ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | Landscape Architects |  | 01/06/2020 |  |  |  |  | Closed | 01/13/2020 | 01/28/2020 | 01/21/2020 | 01/06/2020 | 01/06/2020
90 |  | 0 |  |  | Request for Information | Buttress Clarification at Annex | Reference sheets AE146 and details 5,6/S211. The 4 column buttresses at grid east of grid AC/between A4 to A7 are dimensioned to be 2'-0" wide by 1'-3"deep on AE146. On sheet S100 the detail reference is 5/S211 and 6/S211 has a dimensions width at 18" and edge of concrete at 9 1/2 from CL column. Please confirm the architectural dimensions are correct? Reference the color coated plan S100. The dimensions on AE146 and AE147 are not real clear at all locations. Please verify the concrete dimensions from face of CW4 wall typical (pink 2'-0"x1'-3", north elevation in yellow AE to AF and AC to AD 1'-6"x11", north elevation blue 1'-6" wide x 1'-3" deep grids AE to AD/A10, east elevation "green" 1'-6" wide x 8 1/2" deep grids A1 to A5/ AA to AB). Reference the color coated plan S101A. Please verify the following: Grid AH/ A2 to A5 where the existing wall is capped are the buttresses 1'-6" wide by 11" deep from face of wall? What is the elevation of bottom of buttress at this location per 17/S221? Please provide elevation to bottom of north annex buttresses per detail 16/17/S22. (Note says below frost depth) (EXTRA COSTS COULD BE INCURRED PER THIS RFI) |  | Revised Sheets to reflect width of plinth around annex buttress will be part of a upcoming CCD-34. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/06/2020 |  |  |  |  | Closed | 01/30/2020 | 03/05/2020 | 02/27/2020 | 02/25/2020 | 01/06/2020
91 |  | 0 |  |  | Request for Information | Geo Foam Specification | See attached technical data sheet for structural GEO Foam. Please provide clarification of the foam density required on the project? Specific locations would pertain to details around the baptistry font (6/S241), below elevator slab (3/243). We assumed EPS12 as the typical use spec. |  | See ARW's response ¦ ¦ ¦ EPS12 structural foam is adequate for the locations noted. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/09/2020 | 01/08/2020 | 01/08/2020 | 01/08/2020
92 |  | 0 |  |  | Request for Information | Tree RFI 1 | [5 empty] | Medium | Camron Walker | Westland Construction, Inc. | Westland PE’s | [6 empty] | Closed | 01/15/2020 |  |  |  | 01/08/2020
93 |  | 0 |  | LX101 & C.6 | Request for Information | Redesign Sidewalk to Preserve Trees | (RFIs 1 & 2 for the Tree RFIs Attachment) Chris requested before we remove these two trees we discuss the possibility of redesigning the sidewalk. Please advise. | Either approve their demo or provide redesign. | See attached for updated LX101 showing removal of the tree nearest the sidewalk and removal of the tree in the southwest corner near the seating area and an update to the tree protection fence alignment. Also included is a quick study showing the new route of the sidewalk (see the blue option), a PR will be issued with updated plans for pricing and implementation. ¦ We are working on finalizing the updated plan set for the 400 South improvements and will include the updated plans for the sidewalk modification with that set. Included will be a modified layout plan, grading plan, planting plan and irrigation plan. ¦ ¦ Please provide Dimensions and Radiuses needed for final layout. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Greg Boudrero | MGB+A The Grassli Group | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 02/18/2020 | 01/31/2020 | 01/30/2020 | 01/08/2020
94 |  | 0 |  | LX101 & C.6 | Request for Information | Remove Tree Near Construction Traffic & New Sidewalk | (Tree RFI 3 from the attachment) The tree is too close to the new side walk. Construction access will pass right next to this tree for the duration and we feel the health of the tree will be severely impacted. The protection we currently have around the tree will have to be modified to allow access. | Add this tree to those approved for demo on LX101. | See attached for updated LX101 showing removal of the tree nearest the sidewalk and removal of the tree in the southwest corner near the seating area and an update to the tree protection fence alignment. |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 01/08/2020 |  |  |  |  | Closed | 01/11/2020 | 01/30/2020 | 01/10/2020 | 01/08/2020 | 01/08/2020
95 |  | 0 |  |  | Request for Information | Duct Fire Wrap | Keyed note 5 on M100A issued in CCD 7 calls for “duct between fire smoke damper and entering floor above to be fire wrapped.” However this keyed note is only shown on three different vertical duct runs. Please advise if this keyed note is typical for all similar conditions on this sheet. please see attached |  | See VBFA's response ¦ ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/29/2020 | 01/27/2020 | 01/27/2020 | 01/08/2020
96 |  | 0 | 220000 | CCD#007- MP 100A | Request for Information | Font Skid Relocation HX piping | CCD#007, drawing MP 100A indicates new font equipment to be relocated to crawlspace beneath baptistry. No revision appears to have been made to the Heat Exchanger HX-1 piping and routing and this new location. | Please provide revised Heat Exchanger piping detail for relocated font equipment | See attached revised Plumbing drawings. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/24/2020 | 01/23/2020 | 01/22/2020 | 01/08/2020
97 |  | 0 | 220000 | P099A-CCD#007 | Request for Information | Font Skid Relocation-Drainage Requirement | Per CCD#007, drawing P099A, font skid has moved to crawlspace. No methods appear to be shown to provide system backwash or water spillage in this crawlspace area. | Please advise if a floor sink/drain will be required at this crawlspace location. | See attached from VBFA for clarification. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/24/2020 | 01/23/2020 | 01/22/2020 | 01/08/2020
98 |  | 0 | 220000 | P099A | Request for Information | Laundry floor drain | Laundry floor drain drop between bottom of floor drain and trap weir of the p-trap exceeds 24". | Change the laundry floor drain into an indirect waste, which sleeves through foundation and then ties into a new floor drain in the crawl space. See attached shop drawing for proposed routing and detail. | See VBFA's response ¦ ¦ ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/24/2020 | 01/23/2020 | 01/23/2020 | 01/08/2020
99 |  | 0 | 230000 |  | Request for Information | Allowed duct height at crawlspace | Drawing M100A, is there a minimum clearance height in the crawlspace that needs to be maintained? Duct as shown within the attached shop drawings is located as low as 49" AFF. | Please confirm if this is acceptable, reference attached clouded area. | See VBFA's response ¦ ¦ CRSA does not have minimum height requirements in the crawl space. VBFA, do you see any issues? ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/24/2020 | 01/23/2020 | 01/22/2020 | 01/08/2020
100 |  | 0 | 230000 | M100A | Request for Information | Duct floor penetrations at baptismal font area | Mechanical Drawings M100A indicates Fire Smoke Dampers as shown per the attached clouded details at crawlspace gridline HF. However, the structural drawings show bent plate at the slab edge. This appears to be typical throughout the crawlspace. | Please provide additional detail/direction regarding fire rating of this duct at these locations. | See VBFA's response ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/08/2020 |  |  |  |  | Closed | 01/15/2020 | 01/29/2020 | 01/28/2020 | 01/27/2020 | 01/08/2020
101 |  | 0 | 220000 | P099A | Request for Information | Sump SP 6A/6B elevation | Drawing P099A, sump SP 6A/6B, see attached clouded BIM detail of sump. Invert of 12" dewatering main that is entering the sump is 10" below the "lowest inlet" elevation when sump is placed on the floor as shown in the latest revit model. | Verify elevation of floor as shown in the architectural model. If correct, it would appeat that the sump would need to deepen by min of 10". Also, please confirm 12" penetration for dewatering pipe at gridline HB foundation, see attached. | See VBFA's response ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/09/2020 |  |  |  |  | Closed | 01/15/2020 | 01/29/2020 | 01/28/2020 | 01/23/2020 | 01/09/2020
102 |  | 0 | 230000 | MP100, MP100A, M411 | Request for Information | Hot water heating piping at central plant | Hot water heating piping shown at Mech room 036, drawing MP100, MP100A and M411. Drawings indicate 6" hot water heating piping reducing to 4" after the first lateral TEE serving the south mechanical room 043 and then indicates the pipe increasing back to 6" approximately 10' east of the TEE shown. See attached for reference. | It appears the lateral TEE shown should be sized as a 6"x6"x4 instead of the 6"x4"x6" as modeled. | See VBFA's response ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/09/2020 |  |  |  |  | Closed | 01/15/2020 | 01/22/2020 | 01/22/2020 | 01/22/2020 | 01/09/2020
103 |  | 0 |  |  | Request for Information | Elevator Door and Frame Metal Finish | I would like clarification from the architect on the elevator doors and door frame finishes for each elevator, and for each landing. I would like similar clarification for the elevator cab interior doors & cab fronts and transoms, for each elevator. I know some of the cab fronts have wood paneling on top of my metal, but I need to know what metal finish to provide. |  | Elevator 1 - Service Elevator Door and Frame to be stainless steel Cab is all Stainless Steel - No Millwork Elevator 2 - Annex Patron Elevator Door are Gunderlin Medium Oxide Bronze, Frames are Factory painted White Cab is to be covered in Millwork, Provide Factory painted White cabs Elevator 3 & 4 - West Tower Elevators Door are Gunderlin Medium Oxide Bronze, Frames are Factory painted White Cab is to be covered in Millwork, Provide Factory painted White cabs Elevator 5 - Historic Elevator Door are Gunderlin Medium Oxide Bronze, Frames are Factory painted White Cab is to be covered in Millwork, Provide Factory painted White cabs Additional information will be clarified in CCD 057 - Elevator Cab Updates |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/09/2020 |  |  |  |  | Closed | 01/15/2020 | 06/04/2020 | 06/03/2020 | 05/27/2020 | 01/09/2020
104 |  | 0 |  |  | Request for Information | Historic north jacket wall elevation | Reference sheet S101A and detail 1/S243. Please confirm that the 4 1/2" SOD south of grid A1 will bear on top of the foundation jacket wall? Please confirm elevation 99'-7 1/2" is the top of concrete elevation for this bearing point? |  | See ARW's response ¦ ¦ ¦ Deck bearing at this area is 6-1/2" below elevation 100'-0". The slab in this area is recessed 2" to accomodate floor finishes which is why the SOD is 4-1/2" thick here. ¦ ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/09/2020 |  |  |  |  | Closed | 01/16/2020 | 01/13/2020 | 01/13/2020 | 01/13/2020 | 01/09/2020
105 |  | 0 |  |  | Request for Information | Storm Drain Installation Conflict | We have been notified to impact the Visitor Center as little as possible during early construction as plans may change. We are requesting permission to demo a section of the visitor center plaza as soon as possible. Please see the attachment for planned demo and advise. |  | Owner has accepted the selective demo as proposed in this RFI to allow for the install of utilities. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/10/2020 |  |  |  |  | Closed | 01/13/2020 | 01/13/2020 | 01/13/2020 |  | 01/10/2020
106 |  | 0 |  |  | Request for Information | ADA Benches RM 177 & 168 | Who is responsible for the ADA benches in the Brides ADA rm 168, D/AE4133 and Youth Bathroom rm 177, B4/A4134. There is not detail of this bench and nor a clarification whether these are millwork items or if they should be provided by the locker contractor. |  | See GHID response ¦ Is GHID planning on providing an ADA compliant bench in their furniture package, or shall we select an off the shelf product? ¦ We would like to see potential options from the locker contractor before making a final decision. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Westland PE’s |  | 01/13/2020 |  |  |  | 1.00 | Closed | 03/13/2020 | 03/12/2020 | 02/03/2020 | 03/05/2020 | 01/13/2020
107 |  | 0 |  | AE582, AE620 | Request for Information | Material for Door Jambs & Columns | It is Fetzers intent to use poplar in the following areas, crown moldings, main body of the columns, column crown, arch portion of the door jamb casings. Poplar comes in longer lengths, wider widths and is more readily available than maple. Doors, jambs, base moldings and trims that are low will be maple for durability. See attached sketches for clarity. Respond if this is acceptable. |  | See upcoming CCD-19. ¦ Poplar wood is acceptable. All Crown Molding in the historic building will be plaster. All Crown molding in the Annex building will be GFRG. There will be no wood crown molding. Columns, Arched portals and door jamb casings can be Poplar wood. Maple is acceptable for the Doors, jambs, Base moldings and trims for durability. |  |  | High | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/26/2020 |  |  |  |  | Closed | 02/29/2020 | 04/09/2020 | 04/02/2020 |  | 01/13/2020
108 |  | 0 |  | AD102 | Request for Information | Quatrefoil Columns LVL 2 | Demo drawings AD102 note 2.84 states columns in instruction room B rm. 211, and lobby room 218 columns are to be removed and reused. Drw. A1/AE582 shows these rooms are to receive new columns. Clarify if in rm. 211, 218 full size columns are to be new or reused columns. |  | AD102 note 2.84 Is correct. All existing Quatrefoil columns on Level 2 are to be carefully removed and reused. Only new columns will be provided where originals don't exist. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/14/2020 | 01/13/2020 |  | 01/13/2020
109 |  | 0 |  | AE570, AE571, AE584, AE620, AE621 | Request for Information | Wood Moldings | Many molding in the architect drawings state to match existing profiles in a particular room. It is Fetzers understanding the molding profiles shown in the architect’s drawings have already been digitally scanned and the profiles shown is what is to be made. Confirm if this is correct and there is no need to digitally scan any existing moldings. We do need the CAD drawings requested by email on 01/13/2020. |  | Architect still requests that these profiles be scanned. What is seen in the model is from a 3D scan of the building that accurately located walls and major elements, but lacks the fine detail that is required for millwork. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/30/2020 | 01/28/2020 |  | 01/13/2020
110 |  | 0 |  | AE102, AE4207, AE388, AE389 | Request for Information | Columns Level 2 Vestibule 213, Stairs 5 | Enlarged floor lans B3/AE4207 show columns in rm 213 but no column capital and no reference to column type. Enlarged floor plan A1/AE388 showcolumns in stair well 5 level 2 and elevations AE 389 show no elevations of columns in this room or details. Are there to be columns in this room and if so proved elevations and details? |  | Please see upcoming CCD-042 for revised columns. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 03/19/2020 | 03/16/2020 |  | 01/13/2020
111 |  | 0 |  | AE600 Door Schedule | Request for Information | Door Casing Conflicts | RFI 025, 026 states to refer to door schedule for casing types. Door Schedule Door #010A and #010C call for a wood jamb and casing C1 only on exterior side, no casings listed on interior side. Elevation of room 10, D1/AE4003A, shows casings at these two portals on the interior side which does not match the door schedule. Clarify if casing is required on interior side and casing type. |  | See future CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
112 |  | 0 |  | AE600 | Request for Information | More Door Casing Conflicts | Ante Rm 061, Door 061C and 061C call for C4 casing on exterior and C3 casing on the interior. I believe these casing are listed backwards. All casing in rm 061 should be C4, which match the elevations drawings shown in the room. Please clarify. |  | Refer to the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
113 |  | 0 |  | AE600 | Request for Information | Door Casing Conflicts (Door 068 & 081) | Door 068 calls for casing C3 exterior and C4 interior. Door 081 calls for casing C3 exterior and C4 interior. Both should be reversed, C4 should be the exterior since the baptistry rm 067 has the C4 casing. Please clarify |  | Refer to the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
114 |  | 0 |  | AE600 | Request for Information | Door Schedule Hardware | Conforming set of drawings no longer show a column for hardware types on the door schedule. Previous version of drawings did show hardware schedule. Provide a door hardware schedule. |  | Hardware groups were removed from sheets AE600, AE601, AE602 and as noted only appear in Spec Section 087100.01 & 087100.02 Addendum #6. This was to eliminate duplication of information. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/14/2020 | 01/13/2020 |  | 01/13/2020
115 |  | 0 |  | AE600 | Request for Information | Casing Type RM 020A Mechanical | Room East Mechanical 020A there is a set of double doors next to door 020A. There is no door number for this door nor does this door show on the schedule. Clarify what door number this is and what type of door and door casing. |  | Refer the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
116 |  | 0 |  | AE600 | Request for Information | Casing Door 065A | Door 065A to confirmation room 064 calls for type C1 casing of interior side and C1 exterior side which is a square casing and door type 3 which matches the square casing, however from the confirmation side of this door the door is a type 6 and the casing is a type C4. Should door 065A be type 6 with C3 casing interior to match other casings in the room and C4 exterior casing to match elevation A2/AE4025? |  | Refer to the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
117 |  | 0 |  | AE600 | Request for Information | Casing Door 060A | Door 060A schedule calls for C1 casing interior and C4 exterior. Should this be C4 interior same as casing in room 060? See elevation A2/AE4025 |  | Refer to upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
118 |  | 0 |  | AE600 | Request for Information | Casing Door 060 | Door 060 schedule calls for C4 casing exterior and C3 interior. Should this be reversed, C4 is the casing in room 060. See elevation A5/AE4025 |  | Refer to upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
119 |  | 0 |  | AE600 | Request for Information | Casing Door 082A | Door 082A schedule calls for C4 casing exterior and C2 interior. Should this be C3 exterior to match other casings in the hall way is the casing in room 060. See elevation A5/AE4025 |  | Refer to the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
120 |  | 0 |  | AE600 | Request for Information | Casing Door 080 | Door 080 schedule calls for C1 casing exterior and C3 interior. Should this be C3 exterior and C1 interior? See elevation B3/AE4028 |  | Door casing identification for door 080 on the door schedule is incorrect. Please note change to schedule. Casing C1 to be in room 080 (interior side) and C3 to be in RR Vest. room 079 (exterior side). |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/30/2020 | 01/21/2020 |  | 01/13/2020
121 |  | 0 |  | AE100B | Request for Information | Casing Door RM 053 Elevator Lobby | Elevator Lobby 053 has 2 doors with the same door number 053C. Clarify which is the correct door for door number 53C and provide door type jamb type and casing type for the other door. |  | Refer to the upcoming CCD-19. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 02/13/2020 | 02/13/2020 |  | 01/13/2020
122 |  | 0 |  | AS501 (Addendum 6) | Request for Information | Painted Stainless Steel Addendum 6 AS501 | AS501 Keynote 5.25 "1 1/2" dia. painted stainless steel handrail". Is the railing painted stainless steel? Please verify this is correct. |  | Stainless Steel handrails will not be required to be painted. Keynote 5.25 has been updated. See revised sheet AS501 |  |  | Medium | Matt Fackrell | Accent Painting and Special Coatings, LLC | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/14/2020 | 01/13/2020 |  | 01/13/2020
123 |  | 0 |  |  | Request for Information | Stone Finish | Stone finishes for the sandstone caps and paving are not called out in the landscape drawings or the Spec’s. Please confirm stone finish for site wall caps. fountain caps, and pavers at brides exit. | Site wall and fountain caps honed or polished. Pavers flamed or sandblast. | Stone finishes for wall caps to be honed for both site walls and fountain walls. Stone pavers and stairs to receive a light windswept (sandblast) finish. Submit samples for approval. ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/30/2020 | 01/28/2020 | 01/27/2020 | 01/13/2020
124 |  | 0 | 230000 |  | Request for Information | Volume Damper Clarification | Per verbal conversations with design team, it has been indicated that electronic volume dampers serving registers will only be required in non-accessible ceilings at instruction rooms, ordinance rooms and celestial room. All other accessible ceiling areas/rooms are to be provided with remote cable dampers and position indicators. | Please clarify if the electronic volume damper system is only required at registers located within non-accessible areas/rooms such as instruction rooms, ordinance rooms and the celestial room. | See VBFA's response ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/13/2020 |  |  |  |  | Closed | 01/20/2020 | 01/24/2020 | 01/23/2020 | 01/23/2020 | 01/13/2020
125 |  | 0 | 085200.01 | Wood Windows | Request for Information | Species of Wood for Wood Windows | The wood window material specified for the historical wood replicas for the main the temple and annex project is “Accoya®”. The amount of material required for both phases is quite large and needs to be sourced/purchased and shipped to the US. The lead time for this material can be 12 – 14 weeks or longer. We currently have “Approved As Noted” submittals for the Window Type “C” mock-up for the Annex building which does included the “Accoya®” wood window material as the specified wood material. The intent of this RFI is to CONFIRM the “Accoya®” wood material is / will be same wood material for the historical wood window replicas on the main temple building. This material can be purchased in advance (due to extensive lead time) of the main temple window submittals. |  | Yes, Historic and Annex wood windows are to be Accoya as specified. |  |  | Medium | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 01/14/2020 |  |  |  |  | Closed | 01/21/2020 | 01/30/2020 | 01/21/2020 |  | 01/14/2020
126 |  | 0 |  |  | Request for Information | Baptistery Ceiling Structural Reinforcing | During the demolition process it was discovered that some of the historical beams have had notches cut out of them (See photos below). For locations I have attached the sheet S102 for reference. Please advise as to what needs to be installed in these locations to meet the weight loads imposed on them. |  | See ARW's response ¦ ¦ ¦ Reinforcing and framing required for this condition is included in CCD-16 that will be released shortly. |  |  | High | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 01/14/2020 |  |  |  |  | Closed | 01/19/2020 | 01/30/2020 | 01/23/2020 | 01/21/2020 | 01/14/2020
127 |  | 0 |  | P099, P099A | Request for Information | DW Lines Under Slab | Please advise if the interior DW lines as outlined on Sheets P099 and P099A are required as shown or if it can be reduced or removed. This arose from a conversation between Ryan and Chris. They looked at the system and are curious if the perimeter drain will be able to handle all of the water that could be coming from the DW lines under the slab, or if there is an artesian action that is causing the need for the lines under the slab. |  | See VBFA's response |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/14/2020 |  |  |  |  | Closed | 01/23/2020 | 01/23/2020 | 01/23/2020 | 01/22/2020 | 01/14/2020
128 |  | 0 |  |  | Request for Information | Annex perimeter chamfer profile EL. 100 | Details 12,13,17,18,19,20/S220, 2/S221 Please help locate the chamfer profile size/ dimensions noted on the structural details at the top of the perimeter foundation walls at the annex. Typical note says "see arch. for size and location of reveal". |  | See attached detail showing added chamfer dimensions. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/14/2020 |  |  |  |  | Closed | 01/21/2020 | 02/12/2020 | 02/12/2020 | 01/15/2020 | 01/14/2020
129 |  | 0 |  | S220 | Request for Information | Existing Annex Concrete Wall Clarifications | Were requesting 3 dimensions: On 17/S220 and other annex wall details you show that the existing annex wall will need to be cut down and roughened. How far does it need to be cut down? On 20/S220 shows a beam pocket with a bearing length of at least 3 1/2". How deep should the pocket be in total? (Verify 4" or 6") How far down should the beam bear? (See the attached) |  | Based on a previous RFI, it was proposed that the wall be cut down 20" which is acceptable with Structural. Detail 4/SD200 specifies 17" to 18" (to be field verified). The 17" to 18" was based on information gathered from as-built drawings of the annex. The depth of the pocket will depend on the cut on the foundation wall, the top of beam elevation (verify with Architect), other information provided in detail 20/S220 (i.e. bearing angle thickness). See item #2 response. ¦ |  |  | Medium | Westland PE’s |  | Structural Engineers |  | 01/15/2020 |  |  |  |  | Closed | 01/21/2020 | 01/23/2020 | 01/20/2020 | 01/15/2020 | 01/15/2020
130 |  | 0 | 211000 | AE661 | Request for Information | Sprinkler Head Cover Colors | In order to blend the sprinkler head covers in to the ceilings. Should we paint the sprinkler head covers the same as the surrounding ceiling colors? |  | The sprinkler covers are only allowed to be painted by the manufacturer per NFPA 13 section 6.2.6.2. Whereas the vast majority of this temple is White, please provide a standard white sample of the product to be used to verify if a custom painted sprinkler will be required from the manufacturer. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/21/2020 | 01/23/2020 | 01/20/2020 |  | 01/15/2020
131 |  | 0 | 220000 | P 502, P 099 | Request for Information | SE-1 Sump Dimensions | Drawing P 502, detail 1 indicates sump serving SE-1. This sump is located west of kitchen within annex, drawing P 099. No width dimensions appear to be provided. | Please provide missing dimensions and clarify shape of sump (assume square or rectangular) | See revised detail from VBFA. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 01/24/2020 | 01/23/2020 | 01/23/2020 | 01/15/2020
132 |  | 0 | 220000 | AE 501, AE 528, P 601 | Request for Information | Roof drain body installation methods | Drawing AE 501, detail E1 and drawing AE 528, detail E4 indicate primary roof drain and overflow roof drain bodies installation at differing heights, primary set lower than overflow. The details appear to show the same height of drain collars to be installed at top of roof drain body. This type of installation does not match the 2" high water collar extension indicated on drawing P601 fixture schedule, RDO detail. Also, it is unclear if sump receivers as indicated within the fixture schedule, RD and RDO are to be used. | Please clarify if the architectural drawing details are desired installation method and all primary and overflow roof drains are to be installed at different body heights, and are not to include 2" water dam extension. Clarify if sump receivers are to be used per roof drain fixture schedule. We suggest installing roof drain bodies at same heights, installing 2" water dam collar extensions at overflow roof drains and using the sump receivers as indicated on the fixture schedule, P601. | Please see the attached revised roof drain details. Sump schedule on P601 is correct. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 02/10/2020 | 02/05/2020 | 01/16/2020 | 01/15/2020
133 |  | 0 | 220000 | A and P sheets | Request for Information | Floor drain locations-placements | No dimensions or exact locations of floor drains per the architectural drawings appear to be provided. | Pleaes provide architectural locations for floor drains, see attached for examples. |  |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 03/17/2020 |  | 01/16/2020 | 01/15/2020
134 |  | 0 |  |  | Request for Information | North stonewall and footing sequencing detail 1/S243 | Sheet S100A, 1/S242, 1/S243 1) Detail 1/S243 does not show concrete infill as required around needle beam and basalt excavation on north side of grid H5. Please confirm this detail or will concrete need to be filled around excavation as it shows typical at other locations? 2) 1/S243 it is assumed that the north concrete jacket wall needs to be sequenced first and then the tie rods and needle beams installed prior to load transfer per note shown on detail 1/S242. It appears that detail 1/S243 shows the 24" elevation 90 mat footing pouring against the historic stone wall footings and around the flat jack/ micro piles and the historic stonewall jacket wall placed above. This seems to contradict the direction on the detail note on 1/S242. Please clarify intent? |  | See response from ARW. ¦ ¦ ¦ Question 1 Response: The needle beam will be located at the top of mat slab as shown in the detail. Concrete infill around the beam will be as shown in the most current drawing sets. Question 2 Response: The mat footing can be placed to the side of the jacket wall rather than below the jacket wall. Detail 1/S243 will be revised to indicate this intent. This revision will be included in an upcoming CCD. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 01/29/2020 | 01/24/2020 | 01/24/2020 | 01/15/2020
135 |  | 0 | 220000 | A and P drawings | Request for Information | Roof drain architectural locations | No hard architectural dimensions appear to be given for exact locations of roof drains. A few locations shown conflict with structural members. See attached for clarification. | Please provide architectural locations and dimensions for roof drains, clarify if we can shift roof drains as attached away from the structural members and provide min/max distancing from exterior walls. | See attached CRSA response. ¦ ¦ Brain, can you verify if the shifting and spacing will still work with your design. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 02/13/2020 | 02/13/2020 | 01/27/2020 | 01/15/2020
136 |  | 0 |  |  | Request for Information | Nursery | Since the plant materials were selected by the Landscape Architect prior to bid time, and since the plans require photos of the plant materials to be submitted prior to digging or shipping, will there be a need for the trees and plants to be reviewed in a local nursery storage area prior to planting? |  | The nursery shall supply photos of the landscape material to the landscape contractor and landscape architect prior to shipment for inspection. Prior to shipment of materials the landscape contractor shall inform the landscape architect of the anticipated delivery date and the landscape architect, if available, will come to the site to inspect nursery stock upon delivery and prior to installation. If unavailable, the landscape contractor shall provide images of the delivered nursery stock for the landscape architect to review. It is the duty of the landscape contractor to properly maintain the plant material if they cannot be installed in a timely manner following delivery. ¦ |  |  | Medium | Tim Maynes | Stratton & Bratt Landscaping | Landscape Architects |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 01/24/2020 | 01/22/2020 | 01/15/2020 | 01/15/2020
137 |  | 0 |  |  | Request for Information | Existing Grass | Regarding the existing sod within the Tree Protection Zones, where the grades remain the same, and in the interest of protecting the fine roots of the trees being protected, we are concerned with two items: Removal of the sod could have a detrimental effect on the fine roots of the trees being protected. Tilling the soil amendments into the top 4” of the topsoil will further damage the fine roots, and will damage the larger tree roots. The existing lawn in these areas is beautiful. In the interest of protecting the trees, would it be acceptable to leave the sod undisturbed within the Tree Protection Zones, where the grades remain the same, except where new irrigation or other site work must take place? Those areas will be restored with sod and amended per the specification. |  |  |  |  | Medium | Tim Maynes | Stratton & Bratt Landscaping | Westland PE’s |  | 02/05/2020 |  |  |  |  | Closed |  | 03/30/2020 |  |  | 01/15/2020
138 |  | 0 | 230000 | S 301 | Request for Information | Mechanical Opening at S301 | Drawing S 301, detail C, indicates to oversize a mechanical opening to allow access for a man over duct. No dimension is given. | Please provide a recommended maximum opening dimension for the mechanical opening shown. See attached detail for clarification. | The required opening size needs to be coordinated between Mechanical and Architectural. The width assumed was 50" and the height was assumed as 78". The actual width will be governed by the width of the duct penetrating the wall and will need to be verified with Mechanical. The height will depend on the duct height as well as the desired access height above the duct. This height will need to be coordinated with Architectural and Mechanical. ¦ See Response from VBFA. ¦ The Mechanical opening height between grids AD and AC will need to be 96" high to provide crawl space access above the duct. ¦ ¦ ¦ Brian, can you verify duct sizes so that I can see how much room we have for access? ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/29/2020 |  |  |  |  | Closed | 01/22/2020 | 08/11/2020 | 07/29/2020 | 01/22/2020 | 01/15/2020
139 |  | 0 | 230000 | M100, M602 | Request for Information | IL-4 Louver Size | Drawing M 100, level 0, louver IL-4 is shown to be 48x36. See attached. Drawing M602, mechanical schedule indicates louver to be 36x48. | Please clarify size of IL-4 louver | See response from VBFA. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 01/24/2020 | 01/24/2020 | 01/23/2020 | 01/15/2020
140 |  | 0 |  |  | Request for Information | S100A mechanical opening sizes and elevations | Sheet S100A We need the following information to detail rebar and concrete in the historic area: 1) What are the dimensions and elevations of the south area wells along grid H1/ between HD to HF? The size of the duct shown on the mechanical drawings is 20/14 and 18/18 transitioning to 30/18. What are the clear sizes required through the temple stone wall for these duct penetration? At what elevation is the top and bottom of the duct penetrations clear openings? 2) Along grid HF there are two 36/32 ducts running through the stone wall. Provide clear opening and top and bottom elevations for these openings? 3) Along grid H5 north please provide clear opening dimensions for the (2) 44/30 ducts and (3) 46/32 ducts through the stone wall. It is assumed the bottom of these ducts is at elevation 90' to match the mat slab north of this wall |  | See Response from ARW. ¦ Brian please confirm the sizes below are the actual out side to out side dimensions. ¦ 1. See M100A for modified ductwork sizes. There will be LVL studs through which to run the ductwork. 2. See CCD 28. 3. We suggest using the duct size shown in the drawing plus 3” on all sides, but this should be coordinated via the shop drawing process. ¦ This response will also need to be reviewed and additional information provided by mechanical and arch. 1) See mechanical and arch for dimensions of the area well. Structurally, we are anticipating the following and take no exception to the dimensional requirements of the area well provided they meet the following requirements a. Bottom of the penetration opening is anticipated to be at elevation 90’-0” with the opening being no taller than 36”. b. Shaft opening width is no larger than 5’-0” as shown in detail 9/S240 and the top of the shaft does not interfere with slab on metal deck construction. 2) See mechanical and arch for required dimensions of the shaft. Structurally we are anticipating the following based on detail 2/S242: a. East of the stone wall the top of the shaft opening will be the bottom side of the mat slab in the baptistry level. This puts top of shaft opening at approximately 86’-0”. b. West of the stone wall the top of the shaft opening will be the bottom side of the mat slab in the corridor. This puts top of shaft opening at approximately 86’-7”. c. Shaft opening width is no larger than 5’-0” as shown in 2/S242. 3) See mechanical and arch for required dimensions of the shaft. Meet shaft size requirements shown in details 9/S241 and 9/S240. It is anticipated that the bottom of the shaft opening is at elevation 90’-0”. |  |  | High | Judd Bundy | Innovative Concrete LLC | Mechanical Engineers |  | 01/29/2020 |  |  |  |  | Closed | 01/22/2020 | 03/19/2020 | 03/14/2020 | 02/13/2020 | 01/15/2020
141 |  | 0 | 230000 | M100, M602, AD100, BIM Model | Request for Information | Intake Louver IL-4 and associated components-openings | Drawing M100 indicates fan filter F-DHC-1 associated with intake louver IL-4 as 60x24 in size per equipment schedule. See attached. Drawing M100 also indicates duct coil DHC-1 associated with intake louver IL-4 to be 96x16.5 in size per M602 equipment schedule. See attached. Drawing MP100 does not indicate any hydronic piping serving the DHC-1 coil. See attached. The current BIM model indicates a 36x36 opening at the current IL-4 opening. Field verification has confirmed a 36x108 existing opening. Drawing AD100, keynote 8.07 indicates a new door opening to be coordinated with structural drawings at this louver location. See attached. |  | See VBFA & ARW's response ¦ ARW, can you take a look at Louver 1L-4. It is a 36"x48" Louver going in a 36"x 108" opening and Westland is looking at what needs to be done structurally to infill the remaining hole. ¦ See attached detail 5/S222 for typical concrete infills in existing concrete walls. This detail can be used to reduce the size of the existing opening to what is required for the new louver. This revised detail will be issued in the forthcoming CCD#18 |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/31/2020 | 02/10/2020 | 02/05/2020 | 02/04/2020 | 01/15/2020
142 |  | 0 |  |  | Request for Information | Soda conduit routing | Drawing QF 101 SC indicates a 6" conduit for soda fountain lines routing through slab from kitchen storage 009 diagonal to dining room 012 beverage counter. See attached screenshots. The vertical spacing between mat slab and top slab is approximately 20" and is extremely congested due to sanitary waste and de-watering piping located within this spacing. Specification section 11400, section 3.07 paragraph B-3 states that the general contractor is responsible for wall sleeves for soda lines, etc. | Please review and determine if an alternate route is available overhead or otherwise to avoid under-slab conflicts. | Per CCD 017 - Dewatering Modifications, the dewatering lines have been eliminated from the Annex. It is still VBFA's preference to run the Soda lines below slab. Please review CCD 017 and advise if this is now possible. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 02/10/2020 | 02/05/2020 | 01/17/2020 | 01/15/2020
143 |  | 0 |  |  | Request for Information | Wood Base 4 c4/AE570 | Wood base cannot be brought to a point and stay together. See attachment. Suggestion bring inside radius of wood straight down on to of stone. Top edge of stone may need to be polished |  | Refer to upcoming CCD-19. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/15/2020 |  |  |  |  | Closed | 01/22/2020 | 02/13/2020 | 02/13/2020 | 01/16/2020 | 01/15/2020
144 |  | 0 |  |  | Request for Information | Wood Base Type 1 C1/AE570 | Stone base will not always be consistent in thickness nor will the stone sub be consistent when gluing stone to the wall in the distance from face of stone to face of plaster or drywall. Our wood base wood be made consistent with a 1" rabbet. Is it acceptable to make this wood base with out a rabbet. This way the wood base will sit directly on top of the stone base and if the stone varies in depth from face of stone to face of drywall this will not effect the install of wood base being attached tight to the wall. This will require the stone base to be cut down in height. See attached sketch |  | Please refer to upcoming CCD-19. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/22/2020 | 02/18/2020 | 02/14/2020 | 01/17/2020 | 01/16/2020
145 |  | 0 |  |  | Request for Information | Door 052B door type 21 | Door 052B type 21 states match profiles of door room 316. Room 316 does not show on demo plans so I cannot tell what door jamb details to match and I cannot tell what the width of stiles and rails are for the door to match from detail E4/AE630. Can you give me the location of the door and jamb we are to match or details of the door jamb and the widths of the stile and rails of the door. |  | Refer to the upcoming CCD-19. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/22/2020 | 02/13/2020 | 02/13/2020 | 01/17/2020 | 01/16/2020
146 |  | 0 |  | EP100A, EP101A, EP103, EL604 | Request for Information | Lighting Control Panel Schedules | There are three lighting control panels (LCP’s) shown on the plans: LCP-S1 in Mech. 043 on EP100A LCP-T1B in Elect. 183 on EP101A LCP-T3B in Elect. 302 on EP103 None of these were included in the LCP schedules on sheet EL604 so they were not quoted or submitted on. Are these LCP’s needed? |  | The three lighting control panels mentioned in the RFI are shown on the floor plans and have relays called out and circuited to them, as shown on the lighting circuiting plans. They should all be quoted and included in the project as indicated. Relay panels LCP-T1B and LCP-T3B are also shown on the lighting riser diagram, detail 2, sheet EL502. No bidding questions were received regarding these panels. An updated drawing will be provided to indicate the relay schedules for these panels. ¦ See response in the comments from Scott Hardy from Envision. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/18/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
147 |  | 0 |  | EP105 Electrical Rm 515, EL105B Misc. Circuits, One-line EP7 | Request for Information | Electrical Panel "HE5" | The plans show panelboard “HE5” in electrical room 515 on sheet EP105. No panel schedule is provided and it is not on the one-line drawing so it was not submitted on. Does this panel exist? |  | 2 lighting circuits shown on EL105B should be moved to H3E3 and panel deleted from project. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 01/30/2020 | 01/24/2020 | 01/16/2020 | 01/16/2020
148 |  | 0 | 220000 | P601 | Request for Information | Sanitary waste p-traps | Various requirements appear to be indicated within the construction documents regarding sanitary p-traps, whether they are to be deep seal, have trap primers and/or trap seals (trap guards). Specification section details are as follows: Spec section 221319-14, para 2.2A 8&9 specifies floor drains to have deep seal trap with trap primer connections. Spec section 221319-5, para 2.5B specifies deep seal trap with trap primer connections. Spec section 221319-7, J&K indicates deep seal p trap with trap primer connections. Spec section 221119-12, para 2.12A describes trap primers to be serving p trap connections. Drawing P601 plumbing fixture schedule contains a general note at lower left corner calling for all floor drains and floor sinks to have an elastomeric trap seal (Trap Guard). Installation of deep seal p-traps at underground piping system will require cast iron p-trap and transitioning to sch 40 PVC pipe as PVC deep seal traps are not available. See attached for references. | Please clarify if deep seal traps are required at all underground installations. Clarify if trap primers or trap guards are the desired means of sealing the sanitary p traps. Also, please clarify if deep seal traps are required at historic building overhead locations as this would cause spatial/clearance issues at various locations. | See VBFA's response ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 01/24/2020 | 01/23/2020 | 01/22/2020 | 01/16/2020
149 |  | 0 |  |  | Request for Information | EL 102A Drawing Clarifications | Stair #5 all egress and exit lights are shown circuiting thru H3P3-2 which is a normal power panel. There are 2 lights north side of Rm. 218 (celestial rm) that have no type designation. Rm. 218 Type TLA lights how are they switched and circuited? Do they continue around the curve above the veil? Rm.211 Type TLA lights How are they switched? |  | Drawing revision will be issued to clarify move from normal power to emergency power circuit and relay. The two lights in question are DR6M same as adjacent downlights. It is assumed the room in question here is instruction room B (211) as (218) was not able to be located and the question asks about the veil area. The TLA linear LED fixture is to be continuous through out the entire cove (as shown in the drawings) this includes where it wraps around over the veil area. See arch'l detail that is reference on sheets. TLA fixtures will need to be controlled with dimming control system shown on EL501 and EL503 as separate dimmable/control zone. Drawing revision will be issued for clarification. ¦ Refer to upcoming CCD-21 for Clarification. ¦ ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
150 |  | 0 |  |  | Request for Information | EL 102A Drawing Clairifications | Rm. 210 Type TLA lights how are they to be circuited? All egress and exit lights on this page are circuited thru Panel H3S3 which is a standby emergency panel TYP. they are ran thru a emergency panel such as H3E3. (General) what is the difference between standby and emergency power? I have noticed Exit and Egress lights circuited to either standby or emergency panels. |  | Will be circuited to spare breaker in panel L3S1. Controlled as separate dimmable zone. Drawing update will be provided clarify exact circuit number. All exit signage and code required egress lighting to be on emergency panels. Some spaces have owner requirement for all on during and outage and those non-emergency lights are to be on stand-by only. Drawing revision will be sent to clarify which lights will be on emergency and which will be on stand-by. See response to item 3 above. ¦ Changes will be included in CCD#21 ¦ ¦ ¦ ¦ Scott, Can you provide the revised drawings per your response? |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/13/2020 | 01/16/2020
151 |  | 0 |  | EL 103A, EL 103B | Request for Information | El 103 A&B Drawing Clarifications | 1.Men Instruction lighting run's through relay LCP-L3-7 Woman's Instruction doe's not go thru relay just circuit L3P3B-31 They both have detail LCD_001 from EL 501. Which one is correct? |  | Relay will be needed on Women’s side similar to men’s. Control detail is still accurate to show manual control as well. Drawing revision will be sent for clarification. ¦ Refer to upcoming CCD-21 for clarification. ¦ ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
152 |  | 0 |  | EL 101D | Request for Information | EL 101D Drawing Clarification | 1.Rm. 110 what circuit and relay ar to be used for Type TLA lights? |  | A separate circuit from panel L2P1B and relay panel LCP-A1 will be indicated in an upcoming drawing revision to clarify power and control. ¦ Refer to upcoming CCD-21 for Clarification. ¦ ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
153 |  | 0 |  | EL 101C | Request for Information | EL 101C Drawing Clarifications | Rm. 109 what circuit and relay connect to Type TLA lights? Rm. 166 what Type of indirect linear light? Rm.163,165,166,167,170&171 Egress lights have not been assigned a circuit or relay, Please advise. |  | A separate circuit from panel L2P1B and relay panel LCP-A1 will be indicated in an upcoming drawing revision to clarify power and control. Type TLA, same as other similar locker areas adjacent. They have been circuited and have relay in the plans H1E0-19, and relay panel LCP-A1. Drawing update will be sent to clarify. ¦ Refer to upcoming CCD-21 for clarification. ¦ ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
154 |  | 0 |  | EL 101A | Request for Information | El 101A Drawing Clarifications | Rm. 119 Type TLA lights conected to what circuit and switch? Rm.118 Egress lights are circuited to a standby panel, please advise. Rm. 113 & 114 lights are circuited to a normal power panel, please advise. |  | Upcoming drawing revision will be issued to clarify circuits and relays in question. ¦ Refer to the upcoming CCD-21 for Clarification. ¦ ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
155 |  | 0 |  | ES 200 | Request for Information | ES 200 Drawing Clarifications | Are the relays and circuits correct ? relay panel LCP-A2B is located in electrical rm. 2 which is in the Northwest corner of the annex , panel H3L0 which is feeding relays located in LCP-A2B is located in the south mech. rm. which is at the southwest corner of the Annex and the the lights are at the southwest corner of the site. Relay panel S1 is located next to H3L0 which seems like a better place to control these lights. There is not a separation between LCP-A2B-3 and LCP-S1_8 at the botom left of ES200 please advise. |  | Drawing revision will be sent to adjust circuit and relays to be fed from closer panels as recommended. Drawing revision will be sent to clarify circuiting connections in this area. ¦ Refer to upcoming CCD-21. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/16/2020 |  |  |  |  | Closed | 01/23/2020 | 02/20/2020 | 02/13/2020 | 02/11/2020 | 01/16/2020
156 |  | 0 |  | SD200 | Request for Information | Foundation wall Cut | Yesterday we went around all the remaining Annex walls, we measured several locations along each of the walls. The thickest wall cap edge was 19 inches. Cutting the wall at 20 inches would give a clean uniform edged. The elevation would be 98.4 to top of wall. Please confirm it is acceptable to cut the wall at 20" below the 100 elevation. |  | Structurally it is acceptable to cut the wall as proposed. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 01/17/2020 |  |  |  | 5000.00 | Closed | 01/20/2020 | 01/20/2020 | 01/20/2020 | 01/17/2020 | 01/17/2020
157 |  | 0 |  |  | Request for Information | Annex shaft/area well clarification south of men's dressing | On sheet AE147 there appears to be two open shafts or area well around grids AG-AH and A1-A2. Will these require walls or footings around them? They do not appear on any structural drawings. If applicable please provide details/ clarification. |  | These are a leftover from the Cogen that was removed from the project. It should be showing as a flat slab with no cutouts in these 2 areas indicated. Architect will update sheet and resubmit. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/17/2020 |  |  |  |  | Closed | 01/24/2020 | 01/23/2020 | 01/20/2020 | 01/17/2020 | 01/17/2020
158 |  | 0 |  | MP100, AE100 | Request for Information | Gridlines at A4 and A5 Annex | It appears grid lines A4 and A5 do not match locations on various drawings. See attached screenshot of drawing MP100 and AE100 side by side for comparison. In reviewing the fire protection drawings it appears the grid lines are similar to mechanical in grid line location. The electrical drawings appear to have grid line A4 in the same location as the architectural drawings, grid line A5 appears to match the location of the mechanical drawings. | Please review grid line locations for A4 and A5 grid lines within the drawings and advise which is the correct layout. | Please disregard the gridline locations on the Mechanical drawings. Gridlines on Architectural and Structural drawings are showing the correct locations. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/17/2020 |  |  |  |  | Closed | 01/24/2020 | 02/04/2020 | 02/03/2020 | 01/17/2020 | 01/17/2020
159 |  | 0 | 230000 | M100, S301 | Request for Information | Grid Line AE and AD sheer wall mechanical penetrations | Drawing M100, grid line AE and AD between A5 and A4 there are four (4) 14x8 return air ducts rising from the basement level to level one(1). These are currently shown installed in shear walls. Drawing S301, details A and B give an elevation cut of these shear walls. Detail A appears to have openings to accommodate these ducts but no call outs state this. Detail B does not show any openings. See attached for detail. | Please advise if the openings shown on detail A are meant for these particular return ducts. Advise if detail B will add these openings for the required return duct. If not, please provide an alternate method of installation of the return duct. | See Comment from ARW. ¦ ¦ ¦ The openings shown in A/S301 are intended to be for mechanical ducts. B/S301 will be revised to show duct penetrations noted. This clarification will be made in a forthcoming revision. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/17/2020 |  |  |  |  | Closed | 01/24/2020 | 01/24/2020 | 01/24/2020 | 01/24/2020 | 01/17/2020
160 |  | 0 | 230000 | M001 | Request for Information | VAV inlet connections | Drawing M001, mechanical general note 23 states to use hard pipe with a minimum length of two(2) times pipe diameter for all inlets at VAV boxes. In review of the building model, there are various instances where we cannot achieve the two(2) times pipe diameter distance as noted due to clashes/spacial restraints, but can meet a 1.5 times diameter. The locations are as follows: VAV 2-07A, 2-06B, 0-33, 0-34, 2-10A, 2-04A, 3-06, 0-29, 0-30A and 2-07B. | Please advise if hard pipe connection lengths of 1.5 times the diameter size are acceptable at these listed VAV's. | See VBFA's response ¦ ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/17/2020 |  |  |  |  | Closed | 01/23/2020 | 01/29/2020 | 01/29/2020 | 01/27/2020 | 01/17/2020
161 |  | 0 | 230000 | M603 | Request for Information | Decorative HVAC grille attachment method | Drawing M603, grille schedule calls for the SWS-1 and SWR-1 grilles to have no screw holes. No specification section or detail appears to be provided for installation methods. | Please review attached KEES decorative grille methods of attachment and advise which type of attachment method is approved for use. | Please see Response from Ben Davis - VBFA. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/17/2020 |  |  |  |  | Closed | 01/24/2020 | 03/18/2020 | 03/18/2020 | 03/17/2020 | 01/17/2020
162 |  | 0 |  |  | Request for Information | Existing Trench on East Side of Historic | How are we going to treat this area of existing trench when we install the new storm drain? (See the attached) | We could replace them. We could cap them on either side of the trench with concrete. Please advise. | The tunnels collect water from the roof drains and the perforated pipe around the annex basement. These tunnels will not be needed after the renovation when all roof drains and perforated pipes are in place. Until then, the tunnels need to be able to move water through them, in case of a rain storm event and for groundwater. For now replace them. They need to function similar to how they do now until everything is in place. ¦ Paul, can you address this question? ¦ FYI, This is the response for the existing trench on the East side. |  |  | High | Zac Givens | Westland Construction, Inc. | Clint Foster | Sunroc Corporation | 01/21/2020 |  |  |  |  | Closed | 01/30/2020 | 01/30/2020 | 01/27/2020 | 01/28/2020 | 01/21/2020
163 |  | 0 |  |  | Request for Information | Grid HF needle beam elevation | See attached snap shot from the BIM model. 1) The west historic wall needle beams at grid HF are at a different elevation from the north needle beam. Detail 1/S242 it is assumed that the top of needle beam is around elevation 87' based on the model. Will this work with the sloped 24" slab? 2)We are assuming the north elevation needle beams are at elevation 90' T.O.S. from detail 1/S243 along grid H5. Please confirm |  | See ARW's response ¦ ¦ ¦ 1) The elevation of the top of needle beam being at 87'-0" is correct. Where the 24" mat slab slopes on the west side of the wall, the needle beam will be embeded directly into that slab rather than below as shown in detail 1/S242. 2) The elevation of 90'-0" is correct for the north wall needle beams. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/21/2020 |  |  |  |  | Closed | 01/28/2020 | 01/30/2020 | 01/29/2020 | 01/28/2020 | 01/21/2020
164 |  | 0 |  |  | Request for Information | Fountain Tile material | Please identify tile material and manufacturer for decorative tile inside the exterior fountains |  | 2"x 2" tile will be: Manufacturer: Fujiwa Tiles Type: Celica 293 Colbalt Blue Fujiwa Catalog is attached. We are still trying to determine a manufacturer for the custom 6" x 6" tile and will provide that information as soon as it is available. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 01/21/2020 |  |  |  |  | Closed | 01/28/2020 | 02/04/2020 | 01/31/2020 | 01/27/2020 | 01/21/2020
165 |  | 0 |  | EL 101A, EL 101B | Request for Information | Exterior light elevations a dock | Drawing EL 101A Exterior lighting type SW7A on west wall at dock, What elevation should thease lights be installed? Drawing EL 101B Show what look like 2 exterior lights on grid line AH. If so please provide Light type circuit and relay. |  | We would recommend that these lights be installed around 8'-6" Above floor of door opening and dock roll up door opening, however verify exact heights and alignments along wall with architect. These two fixtures are type SW7A and will be reconnected to existing circuit and relay of similar lighting, to remain, on exterior wall of cooling tower enclosure, facing annex. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 01/22/2020 |  |  |  |  | Closed | 01/25/2020 | 01/30/2020 | 01/24/2020 | 01/23/2020 | 01/22/2020
166 |  | 0 |  |  | Request for Information | Stone Fabrication | Please see attached RFI regarding stone fabrication. |  | We do not have concerns using a different fabricator. Please provide information showing the capabilities of the proposed fabricator. ¦ ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 01/22/2020 |  |  |  |  | Closed | 01/29/2020 | 01/30/2020 | 01/28/2020 | 01/27/2020 | 01/22/2020
167 |  | 0 |  | EP 300 | Request for Information | Lightning protection down leads routing in historical temple | Drawing EP 300 shows 3 Down lead's from air terminals on the roof to ground rods. Can we route the 2 on the east end through the center of the circular stair to the crawl space and drive the ground rod in the crawlspace with a lead that would penetrate the footing to the exterior and connect to the counterpoise loop around the building? Can we route the one on the south side of the building horizontal on a downward angle thru the historical temple protrude the west existing wall into new stair tower and down to ground rod and counterpoise loop from there? Otherwise i believe we would have to notch plaster and stone on the inside from the roof to the crawlspace to accommodate the down lead conduit. |  | It is difficult to understand the exact routing proposed based on the provided description, however an alternate routing may be considered as long as it is follows requirements in Section 264113 Lightning protection for structures, and complies with UL 96, NFPA 780 and is approved by the LPI Certified master installer/designer for this project. No parts of the system shall be visible by patrons and shall not impact the structure. ¦ See responses below. The center of the spiral stairs it not a recommended route ¦ ¦ Brian, are we okay routing these in the same chase (center of spiral stairs) with all that you have in there? Center walls in spiral stairs do not continue up through Level 5, need to make sure routing is clearly identified ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/22/2020 |  |  |  |  | Closed | 01/29/2020 | 01/30/2020 | 01/29/2020 | 01/27/2020 | 01/22/2020
168 |  | 0 |  |  | Request for Information | I-Beam Connection | Please confirm that the I-beams are going to be attached to the Sandstone as shown in the attached sketch and will be incorporated into an upcoming CCD. |  | See ARW's response ¦ ¦ This sketch is correct. This connection will be used at the HSS 16"x4" columns are located and used to support the double wide flange beams. This detail will be incorporated into a forthcoming CCD. |  |  | High | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 01/22/2020 |  |  |  |  | Closed | 01/23/2020 | 01/29/2020 | 01/28/2020 | 01/23/2020 | 01/22/2020
169 |  | 0 |  | S240 | Request for Information | Baptistery Exit Doors | Please confirm that the baptistery exit doors in room 060 are to be cut out of the existing sandstone wall following the existing window lines. In addition to the above that the stone will be able the withstand the loads imposed on it without the structural upgrades as outlined in note 8 on Sheet S240. |  | See ARW's response ¦ ARW - Are these existing openings going to need to be structurally upgraded when going from a window to a door? ¦ This is correct. The openings needs to follow the existing window pattern. Detail 8/S240 does not apply to these door openings and will be removed from the drawings at these locations. We recommend cutting a straight cut down the sides of the opening and then removing the stone so that the existing stone wall conditions can be observed. Once existing conditions can be observed it can be determined if reinforcing of the opening will be needed. Please advise ARW once these walls have been removed and exposed. |  |  | High | Aaron Bolli | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/25/2020 | 01/30/2020 | 01/29/2020 | 01/24/2020 | 01/23/2020
170 |  | 0 |  | AD123, AE123, AE124 | Request for Information | Medallion Center in Room 318 | Please confirm we are not to demo the ceiling of room 318 as shown on the attached drawing from sheet AD123. Please confirm the Medallion in room 318 (Sheet AE123) is to be moved to the center of the room. If it can’t be preserved that a scan and reproduction of the medallion in room 409 (Sheet AE124) is to be made and installed in the center of room 318. |  | Not sure why this is replying back to Innovative Concrete? Please see CCD-11.R.2 showing the ceiling to be removed in room 318. If the medallion cannot be saved and relocated in room 318 a scan needs to be done so it can be replicated. |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/29/2020 | 02/18/2020 | 02/10/2020 |  | 01/23/2020
171 |  | 0 |  |  | Request for Information | Unknown Footings in Basement | Please confirm that the unknown footings found in the historic basement area are to be removed. (see attached photo) |  | See CCD-20 for removal. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/29/2020 | 01/30/2020 | 01/29/2020 |  | 01/23/2020
172 |  | 0 |  | S243 | Request for Information | Buttress Anchor Epoxied | 4/S243- Can the rebar for the buttress pop outs at the west core be drilled and epoxied? If so, what is the embedment requirement? |  | See ARW's response ¦ ¦ Drilling and epoxy is not adequate for these locations. If desired, form saver dowels can be used. Please advise if form saver will be used. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/30/2020 | 02/10/2020 | 02/03/2020 | 01/30/2020 | 01/23/2020
173 |  | 0 |  | S100A, 4/S243 | Request for Information | West Tower Buttress Elevation | At west tower what is the elevation of the buttress popouts? @ grid H1/HH-HG. Reference S100A, 4/S243. |  | CRSA Concurs With Zach Hansen/ ARW. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/28/2020 | 02/27/2020 | 02/25/2020 | 01/23/2020
174 |  | 0 |  | S242 | Request for Information | Needle Beam Elevation West side | West historic needle beams at grid HF. What is the elevation of the top of needle beams? Detail 1/S242 appear to be drawn below the 24” mat slab ramp. How does it transition at the north side where the ramp occurs? BIM model appears to show it at TOS elevation 87’ please confirm. |  | See RFI #168b for response. ¦ See comments, this is answered in a previous RFI ¦ ¦ See Response to RFI 168 for this answer. ¦ I see this answer in RFI 163. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/10/2020 | 02/05/2020 | 01/28/2020 | 01/23/2020
175 |  | 0 |  | AE146B, AE140B, AE160B, S100A | Request for Information | Ramp Slop Going from Historic to Annex | West historic ramp- grid HG, HF what are the dimension to the slope locations? Sheet S100A. Detail AE146B, AE140B does not give dimensions. It appears that the slope happens at the door openings on AE160B. |  | See attached drawing. The ramp extends from opening to opening. See revised T.O.C. elevation and added dimension referencing the length of the ramp. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/30/2020 | 02/19/2020 | 02/18/2020 |  | 01/23/2020
176 |  | 0 |  | S100A | Request for Information | Duct Clear Dimensioning | Sheet S100A at grid HF. The mechanical duct tunnel that runs through the stone wall. On the interior side does this block out turn vertical into the 12” mat slab? What will the clear dimensions need to be for the duct? |  | See VBFA's response ¦ ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/27/2020 | 01/29/2020 | 01/27/2020 | 01/27/2020 | 01/23/2020
177 |  | 0 |  | S222 | Request for Information | Suspended Slab Detail West Tower | S222- many of the suspended slab details at west tower walls were updated to reflect form savers in CCD 2. In multiple locations where we will be pouring each wall lift to the bottom of suspended slab so the slab dowels can be cast in place. Can we use the original conform set structural details for these situations? |  | See ARW's response ¦ see attached ¦ ¦ Those details have been superseded, ARW will provide new revised details in a forthcoming ASI that will show requirements of this new condition. ¦ Please provide the ASI # associated with this response. ¦ Please see attached sheet S222 for revised details. These changes will be issued with CCD#18. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/30/2020 | 02/17/2020 | 02/05/2020 | 02/04/2020 | 01/23/2020
178 |  | 0 |  | S301 | Request for Information | Top of Wall Elevation Grid AE, AD, A1 | S301. Please verify top of wall elevations at grid AE, AD and A1 shear walls. This question was in the shop mark up in RFI 071. It was not answered. |  | Please refer to detail C1/AE503 for AD and AE wall heights. Refer to A4/AE362 for A1 wall height. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/17/2020 | 02/14/2020 |  | 01/23/2020
179 |  | 0 |  | S212 | Request for Information | Slab Rebar Cast in or Epoxied | Detail 3/S212- this detail appears to have a rebar dowel in the slab that is drilled and epoxied. Please confirm this dowel can be cast in with the wall? |  | See ARW's Response. ¦ ¦ This dowel can be cast-in-place with the wall. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/10/2020 | 02/06/2020 | 01/28/2020 | 01/23/2020
180 |  | 0 |  | S243, S242, S241, S240, S212, S101B | Request for Information | Confirm Micropile Sequencing | Micropiles drilled and cased at existing grade elevation (Malcom) Excavate to top of basalt layer (Sunroc) Prep and dowel into existing sandstone/ blackstone walls to top of wall required elevation (interior level 0.5 =T.O.S, exterior north = 99'-5 1/2" detail 1/S243, exterior west=99'-5" details A/S101B, 3/S212) (Innovative) Prep all mechanical/ door blockouts with temporary channels/ sleeves that penetrate stone wall (details 7/S240, 8/S240, 9/S240, 9/S241) Saw cut/ core drill openings as required after temporary support is in place Install all rebar dowels, mats and beams around openings as required Form and pour jacket walls to elevation top of existing basalt grade (1/S242, 1/S243) Would we be permitted to pour taller exterior jacket walls in 2 lifts if we need to? Core drill tie rod holes (Westland) Install and grout tie rods. Plates and nuts installed and tightened Core needle beam locations at stonewall Install steel pipe sleeves and W12x96 needle beams Grout needle beams/ steel sleeves Install flat jacks and begin load transfer jacking after grout has reached strength Grout flat jacks Pour concrete infill around needle beams and around excavation areas as required (1/S242, 1/S243) Mat footings/ slabs will pour against stone wall jacket walls as shown. |  | What is this? Is this an RFI for CRSA or just sequencing for the GC? ¦ Sequencing for GC per Dave Adams. ¦ ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 01/30/2020 | 01/29/2020 | 01/29/2020 | 01/23/2020
181 |  | 0 |  | S100B, S101B, S102, S103, S104, S105, S303, S304, AE345, | Request for Information | Slab Elevations Grid lines HH-HG and H5-H1 | The structural drawings and section cuts do not provide concrete elevations of the suspended slabs in the west tower between grids HH-HG and H5-H1. Reference sheets S100B, S101B, S102, S103, S104, S105. Elevations/sections S303, S304, AE345, AE346. We understand that the slab elevations vary due to floor finishes as shown in the architectural plans. Can we get the top of concrete elevations for all the suspended slabs in the west tower |  | The wood floor thickness is 3/4" thick. Please refer to Section sheets AE345 and AE346 showing the elevation heights. The elevation heights provided are to the top of the finished wood floor of the Historic building. Top of the suspended concrete floor height will be 3/4" less than the elevations shown on the drawings. Even though these elevations are provided to the best of our knowledge, Contractor to field verify with the Historic Building. The intent is to have an even transition wood floor from the new west tower to the Historic Building. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 03/05/2020 | 03/04/2020 |  | 01/23/2020
182 |  | 0 |  | S100A | Request for Information | Slop slab Around Basement Perimeter | Inside historic the top of 12” sloped slab elevation. We assume is at elevation 91’ and slopes to top of 12” mat slab at elevation 87’. Please confirm? Sheet S100A. |  | See responses below. ¦ Architecturally we are showing the slope with 91'-0" & 87'-0" as stated in the RFI. See attached image. ARW, does this match your drawings? ¦ CRSA - Yes this matches our drawings except for the west wall at Grid HF. At this wall, we were not planning for the diagonal sloped floor slab, we were intending for the floor slab at 87' to continue over to the wall. See our detail 1/S242 for this. This was the main reason for the micropiles being installed along this wall line. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/10/2020 | 02/06/2020 | 01/28/2020 | 01/23/2020
183 |  | 0 |  | S100A | Request for Information | Wall Elevation at Grids H1/HD-HF | S100A/9/S240/AE342. What is the top of area well elevation and dimensions of CW-2 area well needed at south side of historic temple? Grid H1/ HD-HF |  | Please see attached drawings. T.O.C. wall elevations are to be 98'-8". See also the attached floor plan showing the size of the wells. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 03/19/2020 | 03/18/2020 |  | 01/23/2020
184 |  | 0 |  | AE140, AE140A, AE140B, AE141, AE141A, AE142, AE143, AE144 | Request for Information | Door Dimensioning | AE140, AE140A, AE140B, AE141, AE141A, AE142, AE143, AE144, multiple door openings do not show dimensions. We would need direction on block out sizes at all door locations? How do we determine if the opening will have a door buck or if we need to oversize to allow the frames to be post installed? This will also apply to the window openings that are applicable at concrete wall locations. (ex. AE651 show waterproofing details, GFRC window surrounds, wood frames etc.) |  | See CRSA's response. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 03/05/2020 | 02/26/2020 |  | 01/23/2020
185 |  | 0 |  |  | Request for Information | Wall dowel detail 2/S221 at electrical room slab | North west electrical room in the annex grids A7/A8 and AH/AF. Reference attached section of sheet S101A and detail 2//S221. Where the 12" and 8" slab dowel out of the CW4 wall and CB7 beam at this location is it acceptable to drill and epoxy the #5 dowels? If so please provide required embedment. |  | ¦ ¦ Epoxy dowels are not allowed at this location. Form saver dowels can be used if desired. Please advise if form saver dowels will be used. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 01/30/2020 |  | 01/28/2020 | 01/23/2020
186 |  | 0 |  | C.8 and LX101 | Request for Information | Storm Drain Tree Conflict | In comparing drawings C.8 and LX101 along with doing the layout, the storm drain line installation and manhole will be interfering with an existing tree. Do we need to reroute the drain line or remove the tree? Please advise. |  | We could move the storm drain line to the north ~15’. We would need to put in a manhole to connect the bend in the pipe. I haven’t looked at the sloped and elevations yet. But we would need to look at those to verify that it will work. By moving this we add 15’ to the pipe. I need to make sure that 15’ isn’t going to mess with the other elevations. There are a lot of moving parts and let me verify this will work. ¦ Tree will be preserved, see update from Civil. ¦ See Horrock's response |  |  | High | Zac Givens | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/23/2020 |  |  |  |  | Closed | 01/28/2020 | 02/18/2020 | 02/05/2020 |  | 01/23/2020
187 |  | 0 |  |  | Request for Information | South Storm Drain Tree Conflict | Equipment operating swing radius will encroach on the trees shown in the attached drawing. It is our opinion that based on the drain location and the equipment that is needed to install it that the trees should be trimmed in order to minimize impact on the trees. |  | Provide tags on limbs that need to be pruned for field review prior to trimming. Are there other equipment options that could be used for this area? ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 01/24/2020 |  |  |  |  | Closed | 01/28/2020 | 01/30/2020 | 01/28/2020 | 01/27/2020 | 01/24/2020
188 |  | 0 |  |  | Request for Information | Top of Micropile Elevation | Please provide a schedule with top of micropile elevation for each micropile. We assume that top of micropile elevation is equal to bottom of flat jack elevation. Please confirm. We would like to incorporate these specific elevations into our design submittal with cut-off detail prior to installation. Please see attached sketch for more information. |  | ¦ ¦ This needs to be coordinated with general contractor who is in control of flat jack requirements. This is outside the scope of structural work. |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | CRSA ARCHITECTURE |  | 01/24/2020 |  |  |  |  | Closed | 01/31/2020 | 01/30/2020 |  | 01/28/2020 | 01/24/2020
189 |  | 0 |  | B4, D5/AE634 | Request for Information | Wood flooring thickness D5, B5/AE634 thickness verification | Meeting held with CRSA, Westland, Fetzers, 1-22-15, it was stated the wood floor would be 7/8" off of concrete. Details of thresholds D5, B5/AE634 notes state there is 2 layers of 7/16" underlayment and vapor barrier( none is shown in detail) then 3/4" flooring. In the meeting it was stated by Westland the flooring from concrete to top of wood floor will be 7/8". Please confirm the thickness of the wood flooring from the concrete to top of wood floor as meeting notes contracted architectural drawings. This is critical to understand the correct step down of casing and jamb from wood floor to concrete, tile or carpet. |  | The wood flooring has been confirmed to be 3/4". Please coordinate casing, jamb, etc. from wood floor to concrete, tile or carpet accordingly. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/25/2020 |  |  |  |  | Closed | 02/03/2020 | 03/05/2020 | 03/04/2020 | 01/27/2020 | 01/25/2020
190 |  | 0 |  |  | Request for Information | Level 5 Ceiling Demo. | Per the phone conversation between David Adams and Kyle Welch please confirm that we are to: 1. Remove the Batt insulation above the ceilings that are being demolished on the 5th. 2. That the ceilings between Gridlines HC and HB along grid line H5 on level 5 are to be demolished. 3. The ceilings above the stair towers can have a wedge shape cut into them to allow the installation of the roof drains, fire sprinkler, lighting protection, etc. I have attached a drawing depicting the locations of the above questions. |  | See CCD - 11. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/27/2020 |  |  |  | 25000.00 | Closed | 01/27/2020 | 02/05/2020 | 02/03/2020 |  | 01/27/2020
191 |  | 0 |  |  | Request for Information | Manhole on Intersection of 500 S & 300 E | We would like to install a sleeve from the manhole on the intersection of 500 S and 300 E to extend out of the intersection onto 300 E. This is so we do not need to cut and patch the new asphalt when it is replaced. | Provide elevations and information to extend the pipe from the intersection onto 300 E. | See the attached pdf (2020 01-31 STORM DRAIN & GROUND WATERPLAN - ONSITE) for information on the pipe. The invert elevation of that pipe will be 2661.26. Sheet C.8 will provide the plan view information. Sheet C.8.1 will provide the profile view information. ¦ See Response. |  |  | Medium | Zac Givens | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/13/2020 |  |  |  |  | Closed | 02/04/2020 | 02/20/2020 | 02/18/2020 | 02/13/2020 | 01/28/2020
192 |  | 0 |  |  | Request for Information | Contractor Office Equipment | It has come to the contractor's attention that there are no 7-Eleven stores within St. George. According to Google Maps the nearest 7-Eleven is 35 miles round trip. Contractor proposes a Slurpee machine to be installed in the Contractor's office to mitigate downtime in prosecution of the work. Note this is a cost bearing RFI. Please advise. | Issue the requisite change documentation. | Approved only if the machine has more than just 3 flavors. Suggestions would be to include Mountain dew, Dr. Pepper and Coke zero. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  | 4890.00 | Closed | 01/31/2020 | 02/12/2020 | 02/06/2020 |  | 01/28/2020
193 |  | 0 |  |  | Request for Information | Existing Annex Out of Square | Attached is Glassey's survey. Not a huge out of square condition inside the Annex – just a few dims that need to be addressed. Looks like the out of square between Historic and Annex is about .5 degrees – resulting in about 12” from East to West on the Historic Temple itself. Let me know your thoughts. We believe it would be better to build the Annex as square as possible with the existing condition and try to make up the out of square with the Historic Temple as they join. We request input from CRSA and ARW on how to proceed. |  | This will be addressed in an upcoming CCD #23 on how to proceed. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  |  | Closed | 01/31/2020 | 02/12/2020 | 02/10/2020 |  | 01/28/2020
194 |  | 0 |  | AE610, AE630 | Request for Information | Door types and Door details AE630 | Door schedule AE600, AE601 calls door types 1, 4, 6, 9, 13, 15, 16, 17, 18 to be 1-3/4" thick doors. These door types on drw. AE610 refer to enlarged section of doors, B3, B4, B5, A5/AE630 to be 2-1/4" thick doors. Door jamb details for these doors D1, D3, D5, B3,A1/AE632 refer to thickness of doors to be 1-3/4". Clarify if enlarged details of doors on AE630 is correct and if doors are to be 2-1/4" thick or if doors are to be 1-3/4" as called out in the schedule. If doors are to be 2-1/4" thick door schedule and door jamb details are incorrect. If door schedule is correct then doors are to be 1-3/4" thick. This will make all the inner door panels only 1/4" thick which I think is to thin of a panel to attach moldings to and to thin for sound purposes. Clarify door thickness and inner panel thickness. | see attached sketch of enlarged door detail. | Refer to upcoming CCD-19 for clarifications. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  |  | Closed | 02/04/2020 | 02/13/2020 | 02/13/2020 | 01/28/2020 | 01/28/2020
195 |  | 0 |  |  | Request for Information | Baptistery Unforeseen | During the demolition process of the Baptistry area we have found the things shown on the attached photos. For clarity I have highlighted the items in Green. Please confirm they are to be removed. |  | Please refer to the upcoming CCD #24. |  |  | Medium | Travis Keenan | TID, Inc. | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  | 15000.00 | Closed | 02/04/2020 | 02/13/2020 | 02/10/2020 |  | 01/28/2020
196 |  | 0 |  |  | Request for Information | Crown Moldings Contradiction in details AE570 verse AE584 | Finish schedule refer to crown moldings show in plaster on drw. AE570. Notes regarding crown molding on AE584 state some of these crown molding are to be wood. It is Fetzers understanding that all crown moldings in this project are either GFRG or plaster based on details in drw. AE6570-AE571 and not wood. Architect was to follow up on this item after millwork meeting 1/22/20 and clarify. The following would be the exception 1. Font 067, Existing beams are to have new wood sides added to the beam. Crown molding A3/AE583 would be wood since top half of crown is suspended in the air and needs to support a light fixture at font ceiling. Detail E3/AE570 says crown is plaster. Which is correct? Trim at the bottom side of the beam A3/AE583 is plaster. 2. Anti Rm. 061, Existing beams are to cover with wood on sides of beam only A1/AE583. Crown molding is plaster. 3. Crown at casework E6/AE570 is wood 4. Instruction Rm 136, 162 Annex, crown molding in room is wood. Crown with slot in crown for air diffuser E3/AE584 5. Instruction Rm 309-314, 322-327 Historical, Box beam is made of wood on top of column. Crown molding E4/AE570 around beam and wall is plaster. |  | This will be part of an up coming CCD-19 regarding revisions to doors, trim and misc. wood work. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  |  | Closed | 02/04/2020 | 03/26/2020 | 03/23/2020 | 01/28/2020 | 01/28/2020
197 |  | 0 |  |  | Request for Information | Annex shop CW2 wall dimensions | Sheets S100, AE146 Please verify the location of the CW2 walls at grids A4-A2 and AF-AG in the shop area. When scaling the structural drawings for the locations of the wall/step they do not match the dimensions on sheet AE146. Please review attached markup plan and sheet AE146 and verify the dimensions in this area. It is assumed the dimension to face of wall/step would follow AE146. |  | Please disregard structural drawing S100 placement of walls and step. The Architectural dimensions on sheet AE146 are correct. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/28/2020 |  |  |  |  | Closed | 02/04/2020 | 02/12/2020 | 02/10/2020 | 01/28/2020 | 01/28/2020
198 |  | 0 |  |  | Request for Information | Needle Beam Dimensions | As we are preparing to fabricate beams and rods for the footings in the Historic Temple Footings it is noted that the lengths will be determined by new concrete interfacing with existing columns that appear to "grow" below finish floor elevations. Please provide overall finish concrete dimensions to allow for accurate beam lengths as well as pipe and rod lengths. | These lengths will be discovered upon the excavation of the existing footings. It has been discovered Via minor excavation (2’) that the Columns appear to be flaring out as they go down. With this in mind they may need to be fabricated long and cut on site to fit the footing when the final width is discovered. | See ARW's response ¦ ¦ Contractor will need to provide dimensions for this. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 01/29/2020 |  |  |  |  | Closed | 02/05/2020 | 02/18/2020 | 02/10/2020 | 02/07/2020 | 01/29/2020
199 |  | 0 |  |  | Request for Information | Finish Concrete Slab Elevations vs Final Finish Elevations | Please provide information regarding final elevations (ie: tile, wood, etc) in reference to slab elevations. Currently the drawings reference finish floors different from the slabs, but slabs do not have assigned elevations. |  | Slab on Deck Elevation is Found on sheet AE146B 95'-1" FFE found on Sheet AE340 95'-3" |  |  | Medium | Brett Glassey | Glassey Steel Works | Westland PE’s |  | 01/29/2020 |  |  |  |  | Closed | 02/05/2020 | 01/30/2020 | 01/30/2020 |  | 01/29/2020
200 |  | 0 | 230000 | M104 | Request for Information | Assembly Room 408-Grilles at floor/bench | Drawing M104, at grid line HF is shown six(6) 50" x 14" FR-1 grilles. Currently this size of grille does not appear to fit under the existing benches where shown to be installed. See attached photos of current dimensions that indicate a clear space of approximately 35 1/2" x 14" under the benches. Please advise. | Recommend installing three(3) 16" x 32" at each location in lieu of 2-54" x 14". | Accepted. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 01/29/2020 |  |  |  |  | Closed | 02/05/2020 | 03/18/2020 | 03/17/2020 | 02/05/2020 | 01/29/2020
201 |  | 0 | 230000 | M105 | Request for Information | CD-4, RG-4 grilles conflict with trusses | Drawing M105, instruction rooms indicate CD-4 and RG-4 grilles to be installed. The minimum ceiling opening requirement for installation of these grilles is 11"x11". The existing trusses only allow for a 10" wide grille. Please advise. | Select a different size grille | It appears that in the celling M105 the CD-4 & RG-4 have enough room to be installed. See the below image. Please clarify question. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 01/29/2020 |  |  |  |  | Closed | 02/05/2020 | 03/18/2020 | 03/14/2020 | 02/07/2020 | 01/29/2020
202 |  | 0 | 230000 | MPD 104, PD 104, AD 104 | Request for Information | Level 4 Mech/Plumb demo | Drawing MPD 104 and PD 104, existing piping systems are called out to be removed. They are located behind existing furred walls. Drawing AD 104 does not appear to indicate any demo of these furred walls. Please advise. | Please advise if the existing piping systems located behind the furred walls is to be abandoned in place or if the furred walls are to be removed allowing the piping to be demoed. | The historic walls are to remain in place therefore the pipes should remain abandoned in place as well. Cap visible ends as possible. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 01/29/2020 |  |  |  |  | Closed | 02/05/2020 | 03/18/2020 | 03/14/2020 | 02/10/2020 | 01/29/2020
203 |  | 0 |  |  | Request for Information | HSS Column Connection Conflicts with Plate Column Connection | RFI 168 provided a connection from new HSS columns to Steel Floor Support Beams. CCD 016 provides a new "Plate Collar" at the top of Stone Columns that appears to interfere with the HSS connection. Please provide direction for this conflict. | Please confirm there is a ½” gap between the vertical HSS and the Sand Stone Column. | See ARW's response ¦ ¦ A 1/2" gap between HSS and stone column is acceptable to allow for clearance of the steel plate collar. |  |  | High | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/02/2020 | 02/18/2020 | 02/10/2020 | 02/07/2020 | 01/30/2020
204 |  | 0 | 230000 | M110A, AD100B, SD100B | Request for Information | Stairwell floor penetration conflict | Drawing M110A, stairwell 7 and 8 indicates two(2) 20" ducts entering the spiral staircase columns and rising up to above floors. Drawing AD100B and SD100B do not show any demo or modifications to the structure to allow for this ductwork at these locations. Following an investigation of the proposed duct path it was discovered that existing basalt footings and beam supports that conflict with the shown path of the duct work. See attached photos and shop drawing that depict the path restrictions. Note the photos were taken of the west side of footings looking east. | Please advise as to how the structure is to be modified to allow installation of the ducts. | See responses from ARW and VBFA along with the attachments. ¦ Please implement mechanical option 2, install the 22/16 duct. ¦ See attached sketch. ¦ ¦ Please advise which or the two option for the HVAC we are to impalement? |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/25/2020 |  |  |  |  | Closed | 04/15/2020 | 05/22/2020 | 05/21/2020 | 05/21/2020 | 01/30/2020
205 |  | 0 | 230000 | M100B, S100B | Request for Information | Level 0.5 structural to mechanical opening conflict | Drawing M100B, along grid line HF, shown two(2) 60" x 24" ducts rising up through floor. Drawing S100B at these same locations indicates a 20" opening for mechanical. The 20" structural opening will not accommodate the 24" duct. See attached for clarifications. | Please advise if it is acceptable to reduce the duct size to 60" x 18" at this floor penetration/opening location and then transition back to 60" x 24" in order to fit through the provided structural opening. | See responses below. ¦ ¦ Brian, can you take a look at the duct size? We can also forward to Zach for him to chime in. ¦ ¦ The size of the penetration can be increased to 24" if needed. Will that still fit in the wall if it is that size? Please verify and advise. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/06/2020 | 02/24/2020 | 02/20/2020 | 02/20/2020 | 01/30/2020
206 |  | 0 | 230000 | M100B, AE100B, S10B, | Request for Information | FSD Actuator locations | Drawing M100B, grid line HF indicates installation of 60" x 24" ducts that have fire smoke dampers shown at the floor level. Drawing AE100B at the same location indicates shower rooms. Drawing S10B shows W10 beams, walls and adjacent mechanical shafts. Due to the constraints of the structural steel, walls and shafts at this location, spacial constraints will not allow installation of the actuators that serve the fire smoke dampers. See attached drawings for clarification. | Please advise if acceptable to locate the fire smoke damper actuators and test switches at level 0.5 and add rated access doors in these walls for service and inspection. See redline drawings AE100B for clarification. due to the proximity to the shower please provide Specs for the access panel. | Refer to upcoming CCD-26. ¦ This was responded in CCD-26. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 05/05/2020 |  |  |  |  | Closed | 02/06/2020 | 05/07/2020 | 05/05/2020 | 01/30/2020 | 01/30/2020
207 |  | 0 |  |  | Request for Information | Drain Line VS Gloria | Please provide an alternate route for the drain line that is running directly under Gloria. We have attached a drawing for reference. |  | There is a CCD that should be coming out today that has the updated storm drain line. This line with be routed to the north to avoid "Gloria's" canopy and protect her the best we can. Look for CCD-06.R2. |  |  | High | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 01/30/2020 |  |  |  | 15000.00 | Closed | 02/02/2020 | 02/20/2020 | 02/12/2020 | 02/05/2020 | 01/30/2020
208 |  | 0 | 230000 |  | Request for Information | Mechanical Louver Schedule | Per conversation with VBFA/Brian Oswald on approximately 1-16-20, it was stated that a revised mechanical louver schedule was to be released. In order to complete the BIM design at the annex basement we are in need of this information. | Please advise if the mechanical louver schedule is to be revised and if so provide detail. Note that this is a high priority RFI. | Refer to upcoming CCD-26 for updated Louver Schedule. ¦ ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/02/2020 | 02/13/2020 | 02/13/2020 | 02/13/2020 | 01/30/2020
209 |  | 0 |  |  | Request for Information | Micropile All Thread Bar | This is a confirming RFI for the all-thread bar required for the micropile installation. Our approved micropile design submittal specifies the use of GR 75 #14 and #18 all-thread bar. A reference to GR 150 steel is made in section 2.2.A of the micropile specification. It appears that the language here, "Where called for on the drawings" is only relevant "IF" GR 150 is required. Please confirm that GR 75, as outlined in the previously submitted micropile design is acceptable |  | See ARW's response ¦ ¦ ¦ Grade 75 is acceptable |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/06/2020 | 02/18/2020 | 02/10/2020 | 02/07/2020 | 01/30/2020
210 |  | 0 |  |  | Request for Information | Epoxy installer certification | Reference structural notes S001 note G-5 and attached information. Per onsite discussion please verify that the installer certification class offered through Hilti will work for the overhead and horizontal epoxy applications on the project. We intend to use Hilti products on the project. Also attached is the information on the class. | please confirm | See ARW's response ¦ ¦ This certification is accetpable. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/06/2020 | 02/10/2020 | 02/07/2020 | 02/07/2020 | 01/30/2020
211 |  | 0 |  |  | Request for Information | Hilti epoxy options into concrete | Reference structural notes S001 In consulting with Hilti Engineers they have a couple epoxy options Hilti HY 100 and Hilti RE 100 with a basis of design comparable to Simpson Set XP. Please review links to attached ESR's and product comparisons. Let us know if they two epoxies will work at concrete applications. We intend to use the specified products at the stone locations. If a phone call is needed with the EOR and Hilti engineer we can arrange. https://www.hilti.com/c/CLS_FASTENER_7135/CLS_INJECTABLE_ADHESIVE_ANCHORS_7135 |  | See ARW's response ¦ ¦ It is acceptable to use HY100 to replace Simpson Set-XP in concrete applications. Stone anchors to be Hilti RE500V3 as noted. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/30/2020 |  |  |  |  | Closed | 02/06/2020 | 02/10/2020 | 02/07/2020 | 02/07/2020 | 01/30/2020
212 |  | 0 |  |  | Request for Information | Doorbell Chime System | See attached master equipment and fixture list from addendum #7. The doorbell chime system is in our electrical specifications, section 262773, but according to the master equipment list the owner provides and installs. Please clarify. |  | Envision Engineering has specified the door/bell system to be provided by DIV 26 contractor complete. Colors/Finishes would need to be approved by architect/interiors. ¦ See comments from GHID. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Interior Designer |  | 01/31/2020 |  |  |  |  | Closed | 02/07/2020 | 05/14/2020 | 05/12/2020 | 02/05/2020 | 01/31/2020
213 |  | 0 | 230000 | M201 | Request for Information | North Stair Tower Return Duct | Previous BIM coordination meeting dated 1-28-20, all parties discussed that the return duct located in the historic north stair tower shaft was to be resized from 36"x80" to 36"x62" from basement to level 3. | Please confirm that return duct located at north stair tower is to be resized to 36"x62" from basement level to level 3. | See response from VBFA. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/03/2020 |  |  |  |  | Closed | 02/10/2020 | 02/18/2020 | 02/18/2020 | 02/14/2020 | 02/03/2020
214 |  | 0 |  |  | Request for Information | Annex level 1 recessed slab missing dimensions | Reference sheet S101A from CCD 16 and AE147. Please provide missing dimensions for slab recesses marked in green on attached sheet AE147. |  | See upcoming CCD #41 showing recess slab locations and clarifications. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/03/2020 |  |  |  |  | Closed | 02/10/2020 | 03/16/2020 | 03/11/2020 | 02/03/2020 | 02/03/2020
215 |  | 0 |  |  | Request for Information | Dimensions for recessed cans and floor boxes | Can we please get dimension Drawings for recessed can lights, smoke detectors, speakers, cameras, occupancy sensors, etc. on the ceilings stating at the 5th level moving down and the basement in the annex moving up. Also dimension Drawings for floor Boxes in these locations. |  | See ASI #34 for locations. ¦ Kyle, Any dimensions of objects in the model would typically not be provided in the electrical drawings. Envision has done a high level of coordination of lighting, wall devices, floor boxes, etc. in their Revit model, however all final dimensions and locations will need to be coordinated with interiors, architect and per field conditions by the contractor. It may be helpful to setup a discussion with the contractor/design team to discuss this topic and review the importance of precise alignment of devices with structure, finishes, etc. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 06/25/2020 |  |  |  |  | Closed | 02/11/2020 | 07/15/2020 | 07/14/2020 | 02/20/2020 | 02/04/2020
216 |  | 0 |  |  | Request for Information | Concrete Vault Sump Pits | US Mechanical is proposing to use the sump pit vaults as per submittal 221323.01 in lieu of the man hole type vaults shown in detail 2/P502. The submitted vaults are detailed at 4” down from top of concrete slab. Also, the lids submitted for these vaults in 221429.06, product 8815, show the discharge lines feeding out through the lid and not through the wall of the vault as shown on 2/P502. Please advise if these vaults are acceptable as submitted and if so, please provide a detail showing how the vaults are to tie into the concrete slab. Also, please advise if it is acceptable to surface mount the lids. See attached sketch and cut sheets for reference. |  | See VBFA's response |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 03/05/2020 | 02/28/2020 | 02/27/2020 | 02/04/2020
217 |  | 0 | 283111 | EY100, EY101, FA-2, FA-6 | Request for Information | Fire Alarm Remote Annunciator | In the submittal review comments regarding the remote annunciation (LOC2) in the main entry we are to resubmit on a smaller, recessed version. “This large version of the remote annunciator will not be acceptable at the front entry/vestibule. If required it would need to be located at the administration office, receiving area or alternate back of house location as approved by AHJ, Owner and architect. Provide smaller, recessed, white version or remote annunciator for entry vestibule as required by local AHJ/Fire Marshal. Coordinate location of fire alarm remote.” There are two annunciators: one in the main entry and one in TFM office 045. The smaller version we will resubmit does not have the emergency voice system for live communications but a large one (LOC1) with this capability is located in the TFM office 045. Are we to just replace the large one in the main entry with the smaller version? Or do we need to relocate the larger one and provide a new, smaller, third one in the main entry? The AHJ will need to weigh in on this. |  | We would recommend that the TFM office remote annunciator remain as is. Our preference is for the smaller recessed remote annunciator (preferable in white if available) to be located in the vestibule (contractor to verify available wall space and exact location as approved by architect). In conversations with AAA fire they will be contacting the AHJ to confirm this is an acceptable solution. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 02/18/2020 | 02/11/2020 | 02/06/2020 | 02/04/2020
218 |  | 0 |  | EC104 | Request for Information | Relocate Data Rack TR4 from RM 402 to RM 515 | After our BIM meeting on 01/28 I would like to propose that we relocate TR4 and any power requirements associated from room 402 to room 515 on the 5th floor. As indicated on Drawing EC104 we have included in our Bid 2-2” conduits from TR1 to each of the individual IDF’s . After investigating and talking with Matt Heaton we believe there is no benefit to locating it on the 4th floor because the 4th floor is at the same level as the 5th floor ceilings. The only downside to this would be the 4th floor data ports at the rostrums on both ends of the Priesthood Room and the Floor boxes (9 locations), which we would suggest to feed from TR3 on the 2nd floor room 202. This would significantly decrease the conduits between the 4th and 5th floors, facilitate adding future locations on both the 4th and 5th floors, and free up a room on the 4th floor for another purpose. Please advise if acceptable and provide any requirements for the modification. |  | It is acceptable to change TR4 from level 4 to Level 5 as described, however the (2) 2" conduits may need to be increased and provided with inner duct. Clarification will be submitted in the upcoming CCD#21. ¦ ¦ |  |  | Medium | Buck Wilkinson | Wilkinson Electric Inc | Electrical Engineers |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 02/12/2020 | 02/11/2020 | 02/06/2020 | 02/04/2020
219 |  | 0 | 064023 |  | Request for Information | Wood base hallways instruction rooms on level 3 and 5 | Existing wood base was removed in these areas at demo time. Is Fetzers to reinstall existing base in these hallways and instruction rooms or are we to make and install new base? |  | This RFI will be clearified in the upcoming CCD-019. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 03/26/2020 | 03/23/2020 | 02/06/2020 | 02/04/2020
220 |  | 0 | 273216 |  | Request for Information | Zetron Radio System Input Points | We are working on the schedule of input points for the Zetron Radio System and need the Temple Engineer's input. These are the points we have: 64 Points Fire Alarm System 24 Points Security System 2 Points Generator Backup System 6 Points AV System 24 Points BAS System 4 Points Combo Telephone/Door Bell 24 Points Future Consult Temple Engineer for his review of these points so we can finalize schedule of inputs. |  | Preliminary points list sent from Envision to Brian Chandler and Korey Talbot for review and comment. Please let us know if additional questions or discussions are needed. It is recommended that Temple facilities managers provide final points based on their use of the project. ¦ This RFI should be directed to the TFM (Brian Chandler). ¦ This RFI should be directed to the TFM Team (Brian Chandler). Thanks ¦ Is there something you need me working on on this? It looks like it is my court for some reason Trask Johnson Project Superintendant 952 East Venture Dr. St. George, UT 84790 (435) 632-0917 Cell (435) 673-9641 Office trask@wilkinsonelectric.com www.wilkinsonelectric.com ¦ Attached is the Temple Points List that we have reviewed and approved to be implemented into the schedule of inputs. Thanks. ¦ ¦ Camron, Has this been forwarded to the TFM team (Brian Chandler)? ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Brian Chandler | CORPORATION OF THE PRESIDING BISHOP OF THE CHURCH OF JESUS C | 04/14/2020 |  |  |  |  | Closed | 04/24/2020 | 06/12/2020 | 06/11/2020 | 04/06/2020 | 02/04/2020
222 |  | 0 | 230000 | M505 | Request for Information | CD-9 Plenum connections | Drawing M505, detail 13 indicates linear slot grille CD-9 plenums to have end connections. The approved Titus linear slot grille does not have an end connection option available. See attached for clarification. | Please confirm if it is acceptable to provide the Titus linear slot diffuser CD-9 with side inlet connections. | See detail 13/M505. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 03/18/2020 | 03/14/2020 | 02/05/2020 | 02/04/2020
223 |  | 0 | 230000 | M104 | Request for Information | Room 409,410, 411 ventilation | Drawing M104, vestibule 409, 411 and Study 410 appear to have no ventilation shown. Please advise. | Clarify whether or not these rooms are to receive some form of HVAC/Ventilation. | See the forthcoming CCD 38 for more clarification. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/04/2020 |  |  |  |  | Closed | 02/11/2020 | 03/18/2020 | 03/14/2020 | 02/05/2020 | 02/04/2020
224 |  | 0 |  |  | Request for Information | Existing 8 inch Metal Pipe at Spiral Stair Cases | Referenced attached sheet PD102. There is an existing 8 inch diameter metal (tin) pipe inside the center chase of both the northeast and southeast historic spiral stair cases that is not shown on the drawings. The pipe was removed from the chases at levels 4 and 5 prior to this project but the remaining levels remain. RR has confirmed the paint coating is lead. Please advise if the remaining sections of pipe from level 3 down should be demoed. | Remove the existing pipe to free up space for the new duct and piping. | Pending architectural permission, the 8" lead pipe should be removed. ¦ ¦ ¦ ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Mechanical Engineers |  | 02/04/2020 |  |  |  | 2000.00 | Closed | 02/11/2020 | 03/17/2020 | 03/14/2020 | 02/18/2020 | 02/04/2020
225 |  | 0 |  |  | Request for Information | Aquatherm Piping | Kory with the TFM group is requesting aquatherm piping in lieu of specified epoxy coated cast iron. Please advise if we are to change to aquatherm piping and at what locations it is to be installed. |  | Please provide pricing to change to NUPI Niron gray electrofusion piping for: All condenser water piping. All domestic hot, cold and recirculation piping with the exception of hot water piping within 50 feet of the water heater which shall remain in copper. ¦ Pricing will be provided for the central plant piping as requested. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Justun Bylund | US Mechanical LLC | 02/05/2020 |  |  |  |  | Closed | 02/11/2020 | 03/19/2020 | 03/18/2020 | 03/17/2020 | 02/05/2020
226 |  | 0 |  |  | Request for Information | Dewatering Detail at Historic Building | Detail 4/P503 shows the dewatering piping in a 20" gravel bed between a rat slab and mat slab. This detail appears to apply to the Annex dewatering that has been eliminated from the scope. However, this detail is also referenced in note 13 on sheet P099A for the Historic building. Please provide a detail for the Historic building detwatering system shown on P099A. |  | Please see the attachment from VBFA. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/05/2020 |  |  |  |  | Closed | 02/11/2020 | 03/05/2020 | 03/04/2020 | 02/27/2020 | 02/05/2020
227 |  | 0 |  | QF101, QF101SCH, P100, EP201 | Request for Information | Kitchen Equip Coordination | The kitchen equipment item numbers on the food service drawings do not coincide with the call outs on the mechanical and electrical drawings. See for example QF101 and QF101SCH versus P100 and EP201. Could we get a coordinated schedule or updated drawings? |  | Yes, These do not coincide because they are from two different consultants with two different formats. This was not intended to have the same schedules. At first glance the information in both schedules seem to be correct. Contractor to coordinate as needed. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/05/2020 |  |  |  | 1500.00 | Closed | 02/12/2020 | 03/05/2020 | 03/05/2020 |  | 02/05/2020
228 |  | 0 |  | M105 | Request for Information | Structural Platform at Each Air Terminal Unit | Please advise if some sort of structural platform is required to be installed at each Air Terminal Unit above level 4 barrel ceiling. See sheet M105. If required, please provide details. |  | A platform would be nice for access but is not required at this time. This response is contingent upon what the owner does with the ceiling. ¦ See CCD-45 per ARWs response. ¦ Please advise as to what the Owner is going to want to do. ¦ ¦ We have been directed to provide catwalks in the attic space. These catwalks will be included in the forthcoming CCD045. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/05/2020 |  |  |  | 1500.00 | Closed | 02/12/2020 | 04/06/2020 | 04/02/2020 | 04/02/2020 | 02/05/2020
229 |  | 0 |  | AE125 per CCD11R | Request for Information | Ceiling Elevations for Level 5 East Rooms | Please clarify if the ceiling elevations called out on sheet AE125 for rooms 517, 518, 519, and both spiral stair cases are correct. It appears the elevations called out would put the new finished ceiling above the existing ceiling joists. Please advise. |  | The ceilings in these areas are not intended to raise above the existing structure. Please see the attached RCP reflecting the revised ceiling hgts. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/05/2020 |  |  |  |  | Closed | 02/12/2020 | 03/05/2020 | 02/21/2020 | 02/05/2020 | 02/05/2020
230 |  | 0 |  |  | Request for Information | North Annex Storm Drain | Storm drain on the North end of the annex is shown going under the entryway. It is my understanding that this is to move North a few feet to stay out from under the slab. Please verify. |  | There is a CCD that should be coming out today that has the updated storm drain line. Your understanding is correct. We will route this to the north to avoid the foundation and will also route it to avoid the tree in the NW corner. Look for CCD-06.R2. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Civil Engineers |  | 02/05/2020 |  |  |  |  | Closed |  | 02/20/2020 | 02/12/2020 | 02/05/2020 | 02/05/2020
231 |  | 0 |  |  | Request for Information | Level 2 Support Beams Elevation Discrepancy | The support beams (W14x68) at level 2 along grids HC & HE are supported by new columns (HSS 14x6x3/8). The beams are meant to bear on the top of the column, but the existing wood beam is lower than the bottom of the new steel beams. This elevation difference does not allow the top of the column to extend to the bottom of the steel beams. Please see attached screenshots and advise. |  | it is acceptable to notch the bottom of the Existing wood beam enough to revive the incoming metal support. (per conversation with Matt McBride on site 02-06-2020) |  |  | Medium | Brett Glassey | Glassey Steel Works | Westland PE’s |  | 02/06/2020 |  |  |  |  | Closed | 02/12/2020 | 02/07/2020 | 02/07/2020 |  | 02/06/2020
232 |  | 0 | 230000 | AE123, AD123, M103 | Request for Information | Duct vs. Lath and Plaster at Level 3 ceiling | Drawing AE123, hallway 316 indicates ceiling height at 9' 2 1/2". Drawing AD123, note 2.106 indicates existing drop ceiling to be removed. This drawing and detail does not address the existing lath and plaster that is located above the existing drop ceiling. Due to existing overhead floor joist height at level 4, new construction to include 3 5/8" metal stud with 5/8 drywall the remaining ceiling spacial opening is 7" 5/8" in height. The existing lath and plaster is +/- 1 1/2" in depth. This leaves a final ceiling spacial opening of 6 1/8". This amount of height will not allow the designed HVAC duct work to be installed in this space. Drawing M103, Duct is shown to be 10x8 (lined), smallest duct can be reduced to is 6" in height due to HTO duct fitting height requirements. This issue is also applicable at rooms 321, 322 and 323. Please advise. | The lath and plaster will need to be removed to allow for the designed system to be installed. | Refer to CCD-11-R.3 instructing to remove the plaster ceiling. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/06/2020 |  |  |  |  | Closed | 02/13/2020 | 02/24/2020 | 02/21/2020 | 02/07/2020 | 02/06/2020
233 |  | 0 |  | CCD-010 EP701 One-Line | Request for Information | CCD-010 One-Line EP701 Clarification | On CCD-10 one-line drawing EP701, there are (19) new 3-pole 20A breakers shown in distribution panel “LDBS”. However, most of these loads look like they should be 120V with 1-pole breakers. Please confirm phase for each new load. |  | Clarifications will be issued in CCD#21. ¦ ¦ |  |  | Medium | Buck Wilkinson | Wilkinson Electric Inc | Electrical Engineers |  | 02/06/2020 |  |  |  |  | Closed | 02/13/2020 | 02/12/2020 | 02/11/2020 | 02/07/2020 | 02/06/2020
234 |  | 0 |  | S245, S221, and S102 | Request for Information | Level 2 I-Beam Spacing | In the floor assembly between the Baptistry and Level 2 it is calling for 2 W14X68, but it does not give the dimension needed between the I-beams. Detail 14 on Sheet S245 shows it being close to the existing 12X24 wood beam, in the BIM it is showing 17 ½” and the complete wall assembly is 18 ½”. For detail and fabrication purposes please advise what the separation between the I beams are? |  | See ARW's response ¦ ¦ The clear distance required between beam flanges is 16" in order for duct work to pass through those beams and into the stud spaces above. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 02/07/2020 |  |  |  |  | Closed | 02/13/2020 | 02/18/2020 | 02/10/2020 | 02/07/2020 | 02/07/2020
235 |  | 0 |  |  | Request for Information | Oversize Holes - Stone Column Wraps | Is it possible to oversize the holes in the 1/2" Plate at the column wraps found on detail 14/S245? We are concerned that these holes will not be able to be drilled in perfect alignment in order to install the through bolts. If oversize holes are not allowed in the plates - is it possible to oversize the core holes? If either option is possible - please provide parameters of acceptable hole sizing. Thank you. |  | See ARW's response ¦ ¦ ¦ Oversized holes are acceptable, however, plate washers will be required in accordance with Structural Note I.6. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 02/07/2020 |  |  |  |  | Closed | 02/14/2020 | 02/18/2020 | 02/10/2020 | 02/07/2020 | 02/07/2020
236 |  | 0 |  | EP601, CCD-010 | Request for Information | Water Fluid Filter Pump P-SS1 Location | Water fluid filter pump P-SS1 was added to the equipment schedule EP601 on CCD-010. Where is this located? What electrical panel and circuit number feeds this? |  | P-SS-1 is located in the existing mechanical 036. It was added as part of Addendum #2 and renamed and HP updated in CCD#10 to match mechanical plans. ¦ See response from Envision and VBFA. ¦ ¦ ¦ |  |  | Medium | Buck Wilkinson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/07/2020 |  |  |  |  | Closed | 02/14/2020 | 02/19/2020 | 02/18/2020 | 02/14/2020 | 02/07/2020
237 |  | 0 |  |  | Request for Information | Annex north shaft wall grid AC and A8 | Reference sheets S100 and S101A, M100. Around grid AC and A8 there is a CW4 wall next to the IL1 louver opening. Sheet S100 is showing this area well wall running west and connecting to the CW4 wall along grid AC. We cannot find a reason for this wall section west of the area well. It is assumed that the way it is shown on S101A is correct. Please clarify. |  | See ARW's response ¦ Correct. This wall is no longer needed and will be removed in a subsequent Addendum to the drawings. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/10/2020 |  |  |  |  | Closed | 02/17/2020 | 02/20/2020 | 02/19/2020 | 02/17/2020 | 02/10/2020
238 |  | 0 |  |  | Request for Information | S301 annex shear wall elevations | We cannot locate elevations to the top of concrete walls on sheet S301. Grid AE, AD and A1. Please clarify. |  | Please refer to the architectural drawings for the required heights of the shear walls. They are shown in the wall section details. ¦ Please refer to Architectural sections A1/AE314 and A1/AE366 showing wall elevation heights. ¦ all needed top of wall heights for shear walls are clearly defined in the architectural wall sections. Please refer to building and wall section sheets. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/21/2020 |  |  |  |  | Closed | 02/17/2020 | 02/28/2020 | 02/28/2020 | 02/11/2020 | 02/10/2020
239 |  | 0 |  |  | Request for Information | CW4 wall reinforcing at annex | S101A and S004 Grid AA and A7 on sheet S101A. What side is the inside face and which the outside face for the vertical dowels at this location? We assume both sides are backfilled. |  | ¦ ¦ Inside face of wall is inside of building face. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/10/2020 |  |  |  |  | Closed | 02/17/2020 | 02/20/2020 |  | 02/17/2020 | 02/10/2020
240 |  | 0 | 260532 |  | Request for Information | Feeder/Branch Circuit MC Cabling | As per spec section 260532-2 sub. sec. 2.1 F (MC/MCAP Cable) And 260532-3 sub. sec. A (Feeders Under 600 Volts) Has the Bid-Alternate for MC VS EMT been approved yet? It has been suggested in BIM Coordination That MC Feeders Be considered Because of Unforeseen Building constraints. Please Advise. |  | Per Owner/Architect MC Cabling is not approved. ¦ ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/10/2020 |  |  |  |  | Closed | 02/13/2020 | 02/24/2020 | 02/21/2020 | 02/18/2020 | 02/10/2020
241 |  | 0 | 220000 |  | Request for Information | Existing Domestic Water at Central Plant-Electrolysis | During the course of decommissioning plumbing systems at the central plant, advanced corrosion has been observed in the domestic water system piping and components. It appears upon further investigation that this corrosion has been caused by electrolysis. Of note, visual inspection of components recently installed as of 2013 still containing small amounts of lead per manufacturing practices seem to have deteriorated in an accelerated manner. See attached photo of existing thermowell where well is damaged and copper is depositing into this device. Preliminary investigation has been ongoing with the help of the owner. Dissimilar metal metal contact was discovered and tested with a galvanometer. | Suggest owner/design review on-site with U.S. Mechanical to determine possible steps to eliminate the potential electrolysis and existing corrosion moving forward. | Please see the pending CCD29 which calls for the replacement of the water heater, softener, PRV, domestic circulation pump, piping and associated systems. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/10/2020 |  |  |  |  | Closed | 02/17/2020 | 03/18/2020 | 03/14/2020 | 02/13/2020 | 02/10/2020
242 |  | 0 | 220000 | P502 | Request for Information | Sump Vaults-Waterproofing | Drawing P502, details 1, 2 and 3 indicate epoxy coated walls in interior of vaults. Due to natural hydraulic pressures from the exterior of vault, it is possible that the interior epoxy coating could "detach" from the interior vault wall and compromise the vaults waterproofing abilities. Please advise if epoxy coating should be installed on the outside of the vault wall. | Please confirm if EXTERIOR epoxy coating of vault walls is desired. | See VBFA's response ¦ Brian, Can you please look at this and get with CRSA to discuss if we need to do additional waterproofing. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/10/2020 |  |  |  |  | Closed | 02/17/2020 | 03/03/2020 | 02/28/2020 | 02/27/2020 | 02/10/2020
243 |  | 0 |  |  | Request for Information | Door Type 4 Door Schedule | Door schedule calls for door type 4 to be 36" wide AE601. Elevation of door types AE610 call for door type 4 to be 40" wide. Which is correct? Stile width of door type 4 AE610 calls for stile to be 4 1/4" wide. Type 1, 2, 6, 9 calls for style to be 4 1/2" wide. Is 4 1/4" correct or should door type 4 be 4 1/2"? |  | For new door construction, follow the door schedule @ 3'-0". There are a few Historic to-be-reused doors at 40" which was the precedent door type. 4-1/2" stiles is approved to bring consistency to the doors. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/10/2020 |  |  |  |  | Closed | 02/17/2020 | 04/16/2020 | 04/14/2020 | 02/11/2020 | 02/10/2020
244 |  | 0 |  |  | Request for Information | CCD 017 Clarification | Reference CCD 017 please clarify the following: 1) What seal coat is specified? Attached is the product data for Spec Chem cure and Seal 25 UV. Is this product acceptable? We assume a 2 coat application 2) Is the specified seal coat for all mat footing applications including the existing mat footing in annex? 3) We submitted 15 Mil Stego vapor barrier and it was approved for the Annex. Confirm this is the acceptable product at both annex and historic. |  | The Seal Coat and vapor barrier proposed by Innovative Concrete is acceptable for use. The seal coat for the tops of all new and existing mat footings. The vapor barrier to be installed at the under side of all 4" rat slabs located above mat footings. Per CCD 017 R.1 - the grooves in the existing mat footing are to be omitted as the slab has a very rough and non-flat surface. The grooves have been deemed useless. Grooves still to be provided in new mat footing. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/11/2020 |  |  |  |  | Closed | 02/18/2020 | 03/10/2020 | 03/09/2020 | 02/25/2020 | 02/11/2020
245 |  | 0 |  | AE141A AE632 | Request for Information | Layout of door openings verses call out door schedule | I noticed some rough opening dimensions listed on the level 1 dimension plan historic and would like to review. See AE141A Door 183 is 3’-0” door type 4 jamb type D5/AE632 Rough opening is 9” greater than the door size making R.O. 3’-9”. Drawing AE141A calls for rough opening layout 3’-4” please advise. Door 184B is 3’-0” door type 4 jamb type D5/AE632 Rough opening is 9” greater than the door size making R.O. 3’-9”. Drawing AE141A calls for rough opening layout 3’-4” please advise. Door 185 is 3’-0” door type 8 jamb type B5/AE632 Rough opening is 9” greater than the door size making R.O. 3’-9”. Drawing AE141A calls for rough opening layout 3’-4” please advise. Door 188 is 3’-0” door type 11 jamb type A6/AE632 Rough opening is 5” greater than the door size making R.O. 3’-5”. Drawing AE141A calls for rough opening layout 3’-1 ½” please advise. |  | This was part of a discussion at an on-site meeting last week with Fetzer's and has been answered. Please close out. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/11/2020 |  |  |  |  | Closed | 02/18/2020 | 05/05/2020 | 05/05/2020 | 02/12/2020 | 02/11/2020
246 |  | 0 |  | EY502 Riser Detail #1. | Request for Information | Antenna Location for Wireless Radio System | Provide location of wireless radio antenna. See note #6, riser detail #1, sheet EY502, | Kory Talbot, Temple Facilities Manager, says it works best on the annex. They relocated the old one from the historic building to the annex to get better reception. | Antenna quantity and exact locations will need to be determined by the radio system integrator (factory representative) based on signal strength and analysis of the building construction such that complete coverage throughout all parts of the building and temple block is provided. Most likely multiple antennas will be required at different locations. See additional requirements in specification section 273216. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 02/11/2020 |  |  |  |  | Closed | 02/18/2020 | 02/20/2020 | 02/20/2020 | 02/18/2020 | 02/11/2020
247 |  | 0 |  |  | Request for Information | Celestial elevator 5 pit elevation | Reference AE337, 8/S241. Is the elevator pit slab at elevation 91? Does it match the top elevation of the slope slab at the east side of historic? If not please provide elevation and dimensions and size of the sump. |  | The floor of the Elevator pit is the top of the Mechanical slab at 87'-0". ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/13/2020 |  |  |  |  | Closed | 02/16/2020 | 03/25/2020 | 03/20/2020 | 02/13/2020 | 02/13/2020
248 |  | 0 |  | AE340, AE 341, AE342, S203, S241, S100B | Request for Information | De-Watering Historical Base | Please see the attached Drawings ( AE340, AE 341, AE342, S203, S241, S100B) I have taken my best guess as to what they mean but am unable to find information on the Drainage Gravel or any filter fabric under the slab. It may be that the Structural Fill will provide the Drainage needed but it seems like we would still want some fabric filtering out the soil partials, so they don’t go down the dewatering system. Please advise |  | See CCD-17.R.1 - Altering the De-watering system and showing the added under slab vapor barrier for this area. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/13/2020 |  |  |  |  | Closed | 02/16/2020 | 03/19/2020 | 03/18/2020 |  | 02/13/2020
249 |  | 0 |  | AE141, D5/AE632 | Request for Information | Door 155 jamb type D5/AE632 | Door 155 calls for jamb type D5/AE632 which is a paneled door jamb. The wall type that this jamb goes into is type 32 is only 7 1/4" thick AE141, and is not wide enough for a paneled door jamb. This wall type needs to be wider to allow for a paneled jamb. I believe this should be wall type 37. Please confirm the correct wall thickness, wall type at door 155. Similar problem at door 156. Dimensional drawing AE141 show a double wall but does not call out wall type at this location. |  | Wall Type 37 to be used at both Door 155 & Opening 156. Plans have been updated to reflect a thicker wall. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/13/2020 |  |  |  |  | Closed | 02/20/2020 | 04/16/2020 | 04/14/2020 | 02/14/2020 | 02/13/2020
250 |  | 0 | 230000 | MP101 | Request for Information | Lobby 131 Hydronic Piping | Drawing MP101, elevator lobby fan coil FC-EV-2 does not appear to indicate any hydronic piping serving this equipment. | Please advise on piping routing and size. See attached drawing for clarification. | Pipe size for fan coils FC-EV-1 & FC-EV-2 is ¾”, See CCD 38. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/13/2020 |  |  |  |  | Closed | 02/20/2020 | 03/18/2020 | 03/14/2020 | 02/18/2020 | 02/13/2020
251 |  | 0 | 230000 | MP103 | Request for Information | Electrical Room 315 hydronic piping | Drawing MP103, electrical room 315 indicates new equipment FC-EV-5. No hydronic piping appears to be shown serving this equipment. | Please provide pipe routing and pipe size for this location. | Pipe size to Fan coils FC-EV-5 and FC-3-10 are 1”, see CCD 38. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/13/2020 |  |  |  |  | Closed | 02/20/2020 | 03/18/2020 | 03/14/2020 | 02/18/2020 | 02/13/2020
252 |  | 0 |  |  | Request for Information | Basement Ledge Wall Removal | Please confirm that per a conversation on site between David Adams and Zack Hansen on 02-13-2020 that we are to remove the ledge wall as shown on the attached drawings. |  | The assumption is also our belief. Please verify that the rock is not intergral with foundation wall and can be removed without damaging historic foundation wall. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/14/2020 |  |  |  |  | Closed | 02/20/2020 | 02/18/2020 | 02/14/2020 |  | 02/14/2020
253 |  | 0 |  |  | Request for Information | Stain Grade Casework Door Profile | Current casework door profile B2, C2,/AE583 shows the profile of the rail of a door coming to a point. I cannot make a rail portion of a door come to a point or mitered edge. The wood will break off at the beveled edge of the rail. I need to have a step in the profile. See attached sketch. Is it okay to modify the profile of the casework doors to have a 1/8" step. Provide finish samples for the stain grade casework for this project. Please specify the p-lam color to be used in the laundry room 028, shop 042, custodial supply 007, and anywhere else p-lam may be required |  | Casework door profile sketch showing 1/8" step is acceptable. GHD group will provide stain finish and p-lam samples. ¦ Stain Finish was provided with wood floor sample. P-lam to be: Wilsonart, Premium laminate Columbian Walnut 7943k-07 Textured gloss finish AEON scratch resistance. ¦ |  |  | High | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 12/03/2020 |  |  |  |  | Closed | 12/06/2020 | 12/17/2020 | 12/11/2020 | 12/03/2020 | 02/14/2020
254 |  | 0 |  |  | Request for Information | Annex dowel detail 3/S221 | Reference sheet S101A at grid AH/A6 detail 3/S221. CCD 13 provided the embedment depth for the dowel into the existing floor but it does not provide a bar size and spacing. Please clarify |  | Dowel to be a #4 @18" o.c. - see detail13/S220 for sim condition. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/17/2020 |  |  |  |  | Closed | 02/22/2020 | 02/20/2020 |  | 02/19/2020 | 02/17/2020
255 |  | 0 |  |  | Request for Information | Micropile Testing | Malcolm Drilling will be installing the two sacrificial micropile test piles this week. Once the micropiles have been installed, cured and tested, the results are typically communicated by us directly to our designer for approval. Logs from the field are sent directly to the designer, who reviews the information right away. Upon this review, if the results are acceptable, we are released into production. Other than written approval from the micropile designer, will the design team require anything else prior to Malcolm moving into micropile production work? |  | The sequencing of this and when Malcolm proceeds with work is at the discretion of the general contractor. We ask that the written approval and test results be submitted to the design team for reference and documentation. ¦ See ARW's response. |  |  | Medium | Matt Madsen | Malcolm Drilling Co Inc | CRSA ARCHITECTURE |  | 02/17/2020 |  |  |  |  | Closed | 02/24/2020 | 03/05/2020 | 02/25/2020 | 02/17/2020 | 02/17/2020
256 |  | 0 |  |  | Request for Information | P_lam Casework | Please specify the p-lam color to be used in the laundry room 028, shop 042, custodial supply 007, and anywhere else p-lam may be required |  |  |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Westland PE’s |  | 02/17/2020 |  |  |  |  | Closed | 02/24/2020 | 02/18/2020 |  |  | 02/17/2020
257 |  | 0 |  |  | Request for Information | Finish Sample Stain Grade Casework | Provide finish samples for the stain grade casework for this project |  |  |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Westland PE’s |  | 02/17/2020 |  |  |  |  | Closed | 02/24/2020 | 02/18/2020 |  |  | 02/17/2020
258 |  | 0 |  | SD102 | Request for Information | Stair 2 Demolition | Due to the way the floor was assembled (Photo Above) should we plan on removing all of the flooring and floor joists in the clouded area. Its not possible to maintain the flooring due to the manner of construction of the existing stair. Please confirm. |  | The existing framing can be removed and new framing will be specified to replace it. This new framing will be shown in the forthcoming CCD23. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/18/2020 |  |  |  |  | Closed | 02/20/2020 | 02/20/2020 |  | 02/20/2020 | 02/18/2020
259 |  | 0 |  | SD105 | Request for Information | North and South Stair Roof Drains and Lighting Protection | In order to run the Roof Drains and the Lighting Protection please advise if we can remove the bump down shown above then rebuild it a larger size. The existing Bump Down was used for plumbing in the past but it doesn't look like it will be big enough for the Drain and Electrical lines we need to run through it. |  | Fur down the whole landing 4" to accommodate space for the drain and lightning protection. Provide an even ceiling transition at under-side of the landing. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/18/2020 |  |  |  |  | Closed | 02/21/2020 | 03/26/2020 | 03/20/2020 |  | 02/18/2020
260 |  | 0 |  |  | Request for Information | Plaster Medallions | Throughout the annex and the historic building we are going to install plaster medallions of various sizes. Going through the drawing there are multiple areas where one room scales to 20" and the adjacent room scales to 18" or 22". Scaling off the drawings there are 11 different sizes and three different styles. Can we talk with the designers and standardize the sizes to a small, medium, and large? I would propose the following: Small-20" Medium-38" Large-72" This change would help us have a clear definite dimension to start prefabbing Medallions and keep things organized to streamline the installation process. |  | Please do not scale drawings for medallion sizes. all medallions are tagged with a type and radius dimension on respective enlarged plans, elevations and RCP's. the majority of these sheets are found in the 4,000 series. each is referenced from the floor plans. A soon coming CCD will clarify that all medallions in the annex are to be constructed of GFRG and the medallions in the historic building are to be constructed from plaster. ¦ Upcoming CCD will also modify some locations and quantities of medallions ¦ See CCD 019 ¦ |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 06/29/2020 |  |  |  |  | Closed | 02/25/2020 | 07/08/2020 | 07/07/2020 | 02/19/2020 | 02/18/2020
261 |  | 0 | 230000 | M100A | Request for Information | Exhaust duct FSD at level 0, grid HH and H2 | Drawing M100A, gridline HH between gridlines H2 and H3, indicates a 20" x 16" exhaust duct that does not appear to indicate an installed fire smoke damper (FSD). The supply air duct adjacent to this exhaust duct does indicate a FSD to be installed. | Please advise if the exhaust duct shown is to have a fire smoke damper. See attached drawing for clarification. | See CCD 38, for fire smoke damper location. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/18/2020 |  |  |  |  | Closed | 02/25/2020 | 03/18/2020 | 03/14/2020 | 02/21/2020 | 02/18/2020
262 |  | 0 |  | S100 | Request for Information | Mat Slab Infill | On grid A4/AF there was an old elevator pit. There is no provision in the drawings for how we should infill. Please advise. | Fill it with concrete similar to the mat slab. Provide required rebar details. | See ARW's response ¦ please see response and detail from ARW ¦ There are two options: 1) Fill the old pit with structural fill similar to the fill that will be used on top of the mat slab. No concrete is necessary. 2) If water proofing is a concern. Infill the elevator pit with concrete per the attached detail. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/26/2020 |  |  |  |  | Closed | 02/26/2020 | 03/02/2020 | 02/28/2020 | 02/25/2020 | 02/19/2020
263 |  | 0 |  |  | Request for Information | Elevator Pit Clarifications (sump, elevation & embedment) | Please see the attached pdf for clarification, but we have three questions: S100 shows a sump in the elevator but it isn't shown anywhere else S100 and AE146 show different elevations for the top of slab On 7/S211 we need to know the dowel size, spacing & embendment |  | Sump size at 18”X18”X18” minimum is needed for temporary sump pump placement. In the event of water collection in the elevator pit a temporary sump pump and hose system install in the sump. ¦ ARW, Can you address #3, then forward to VBFA to comment on #1? - VBFA - 85'-0" is mislabeled as it is tagging the top of the Mat Slab. Top of Pit slab is the existing elevator pit @ 83'-6" as seen on Structural Drawings - ARW ¦ Response to #3 - Use #3 dowels at 12"o.c. w/ 6"min. embed. The dowels need to be long enough to lap over the slab reinforcing the length specified in the rebar lap splice schedule. ¦ |  |  | Medium | Camron Walker | Westland Construction, Inc. | Jay Webster | Westland Construction, Inc. | 02/19/2020 |  |  |  |  | Closed | 02/26/2020 | 03/18/2020 | 03/14/2020 | 03/18/2020 | 02/19/2020
264 |  | 0 |  |  | Request for Information | Mainline Pipe | Sheet LI100 and LI101, in the Irrigation Schedule, indicates that the 4” Irrigation Mainline is to be PVC Class 200 SDR 21, but details 9/LI501, 10/LI502, and 1/LI503 indicate the Irrigation Mainline is to be SCH 40 PVC. The specifications in section 32 84 00, 2.2, C. Pipe, Pipe Fittings, And Connections: indicates that Pressure Lines shall be SCH 40 PVC for pipe less than 3” diameter, but do not specify for above 3” diameter. Additionally, the irrigation as-built drawings for the Temple indicate that the existing Irrigation Mainline which is to remain around the Visitor Center, and to which we are to connect, is SCH 40 PVC. Russ with Sunroc confirmed that when they crossed the existing Irrigation Mainline, it was SCH 40 PVC. PVC Class 200 SDR 21 has a pressure rating of 200 PSI, and SCH 40 PVC has a pressure rating of 220 PSI. Our preference would be to use SCH 40 PVC for the 4” Mainline pipe to maintain uniformity around the project, and for ease of maintenance in the future. In the 4” size, these two pipe classes are essentially the same price. So, this would be a no cost clarification. I discussed this with Brandon Ruiz with MGB+A prior to submitting this RFI, and he indicated that SCH 40 PVC would be acceptable in his opinion for the 4” Irrigation Mainline for this project. Is SCH 40 PVC acceptable for the Mainline Pipe on this project? |  | RFI Response: Per our phone discussion we would be agreeable to 4” mainline switching to PVC SCH 40. Please make the change for all mainline on the project to be PVC SCH 40. Brandon Ruiz, MGB+A ¦ ¦ |  |  | High | Tim Maynes | Stratton & Bratt Landscaping | Landscape Architects |  | 02/20/2020 |  |  |  |  | Closed | 02/23/2020 | 02/25/2020 | 02/25/2020 | 02/25/2020 | 02/20/2020
265 |  | 0 |  | ES101 | Request for Information | Site Electrical receptacle mounting Detail | Drawing ES101 has a detail 2 for wall mounted receptacles there is not a detail for receptacles in planters |  | See attached revised sheet ES503 with added Waterproof in-use duplex receptacle mounting detail to be used in all locations where site outlets are located in planters. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/20/2020 |  |  |  |  | Closed | 03/06/2020 | 03/04/2020 | 03/04/2020 | 02/28/2020 | 02/20/2020
266 |  | 0 |  |  | Request for Information | CCD 18 East Rooms Questions | 1. In the rooms to the east of the Baptistery it has been discovered there are ledges similar to the ones in RFI - 252 Basement Ledge wall Removal. Please advise if these are to be removed as well. 2. Please advise if the door used in for floor 1.5 is to be in-filled with concrete as Shown on Sheet S240 detail 10. 3. if these rooms are to be constructed similarly to the basement under the Baptistery. Will they need to access the area to the east of the baptistery different then what is shown in the photos? if so please advise as to the locations and sizes. 4. S100A shows the Slab in the baptistery basement as being 12" thick with #5 at 6" O.C. Please advise if the basements on the east side Added in CCD18 are to be constructed similarly. If there is a change, please provide. 5. The Basement under the Baptistery floor is called out to be 87'-0" on sheet AE146A. Please confirm these east basements are at the same level. If not, please advise. |  | The following are ARW's response to this RFI. Westland-Please do not proceed with any of this work until it has been reviewed and verified by the Architect. The unattached ledges should be removed as with other locations so the concrete jacket can be placed. In the east tower areas, the depth of the excavation does not need to increase beyond what is there unless needed for mechanical purposes. Cut the sides of the opening from the bottom of the existing opening all the way to the footing. The spaced above the new door will be infilled with concrete per detail 17/S245. Provide a 12" deep of reinforced concrete beam directly above the opening per 17/S245. The new opening will be approximately 4'-10" in width in order to provide approximately 8" of new reinforced concrete jamb on each side of the opening. A horizontal cut at the top of the new opening will be required on each side in order to make the new opening wide enough. Provide a 12" deep reinforced concrete beam directly across the new opening per 17/S245. The remaining height of existing opening above the concrete beam can be infilled per the typical detail 10/S240. These rooms in the east tower area are not required to be excavated to the level of the basement under the baptistry. Access to the areas under the east tower can be achieved by removing the walls below the existing door ways in these rooms. Removal of these walls should allow access to these areas. There is no slab required in the basements of the east tower rooms. If a dust/mud slab is desired by owner, then a 3"-4" unreinforced slab on grade is adequate. A thicker mat slab is not required in this area. The east basements do not need to be excavated down beyond what is existing unless needed for mechanical purposes. ¦ Please refer to comments/ response from ARW. We do not want to make the openings much wider that what is shown on the attached images. ¦ Please see attachments from ARW and CRSA. Existing cuts made at the opening to the stone wall has been reviewed and confirmed to be carefully removed down to the top of the concrete footing (see attached sketch). Concrete jacket walls are to be carefully removed back to the stone wall down to the top of the concrete footing ledge. Please see the previous responses to the additional items in this RFI. ¦ ¦ ¦ See comments from Zach ¦ ¦ See attached revised east wall opening detail. ¦ Please up date your response. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/21/2020 |  |  |  |  | Closed | 02/29/2020 | 03/04/2020 | 03/04/2020 | 03/03/2020 | 02/21/2020
267 |  | 0 |  |  | Request for Information | Elimination of Grooves in Existing Mat Slab | Please confirm the conversation on-site yesterday 02/20/2020 that removed the grooves in the mat slab. The direction is to pressure wash and seal the slab. |  | Yes, This is correct for the Existing Mat Slab. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/21/2020 |  |  |  |  | Closed | 02/28/2020 | 03/12/2020 | 03/11/2020 |  | 02/21/2020
268 |  | 0 |  | S240 | Request for Information | Information on Filling Holes in Stone Walls | Please advise as to how smaller holes in the stone walls are to be filled. For reference I have included a drawing and some CAD elevations. |  | All existing holes in stone walls are to be grouted solid with either concrete or a solid non-shrink grout. Please reference Footing and Foundation Note #3 on Sheet S100A ¦ ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Judd Bundy | Innovative Concrete LLC | 02/21/2020 |  |  |  |  | Closed | 02/28/2020 | 03/23/2020 | 03/19/2020 | 03/23/2020 | 02/21/2020
269 |  | 0 |  |  | Request for Information | Scaffold for Center of 4th Floor | There are, in total, (4) outer legs and (6) inner legs contacting the ground on this project. The for the 20 ft. system shown in the drawings, the max anticipated loads to the legs are 1,500 lbs. to each outer leg and 2,000 lbs. to each outer leg. This results in 18,000 lbs. of load for the 20 ft. x 32 ft. Traversing HAKI Dancefloor system, with the 10 psf. Live Load uniformly distributed across the entire platform deck (approx. 8,000 lbs. of Live Load from loading the deck). The weight of only the Dead Load of the RevB system, then the load is approx. 10,000 lbs. for the system. Please note that these load numbers have been rounded up. We have reached out to the Scaffold manufacturer asking if their system can have bearing points at 15 feet for their Triangular Rail. This would place the Bearing points over the Floor Trusses |  | See Response from ARW ¦ We cannot provide a complete response to this until we know if the manufacturers rail can span from floor truss to floor truss. If the rail cannot span from floor truss to floor truss then the scaffold will overload the existing floor joist. The floor joist are not adequate for this load. Please advise. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/21/2020 |  |  |  |  | Closed | 02/28/2020 | 03/11/2020 | 02/25/2020 | 02/25/2020 | 02/21/2020
270 |  | 0 |  |  | Request for Information | Sidewalk Clarifications | See the attachment for further clarification on these four questions: We are concerned with cutting concrete joints on a radius. Verify concrete finish Dimensions for the sawcut layout Verify light lines mean sawcut and dark line means control joint |  | Proceed with 1/4" tooled joints for control joints and banding (only along the curvilinear walkways, see sketch) outside edge and at expansion joints to be 1/2" tooled joint. All straight walks, plaza areas, and those with paver bands will remain as specified with beveled sawcut joints. Concrete finish is to be medium sandblast across surface of walkways. See details 1 and 3, sheet LL501. See CCD6.R2 for dimensions of control joints and banding. This is correct, the dark line is the expansion joint and the light line the control joint. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 02/21/2020 |  |  |  |  | Closed | 02/28/2020 | 03/05/2020 | 02/27/2020 | 02/25/2020 | 02/21/2020
271 |  | 0 |  |  | Request for Information | LCP-A1B Added in CCD-021 | Relay panel LCP-A1B was added in CCD-021 but the schedule is missing on sheet EL604. Sheet EL502 (LCP revised diagram) is also missing. Please provide sheet EL502 and relay panel schedule for new LCP-A1B. |  | See attached revised sheets with schedule included and revised riser. ¦ Reviewed and noted. Thanks. |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/05/2020 |  |  |  |  | Closed | 02/28/2020 | 03/19/2020 | 03/18/2020 | 02/25/2020 | 02/21/2020
272 |  | 0 | 221319 | P099 | Request for Information | Backwater valve locations | Review drawing P099 markup for three (3) locations at Annex of proposed backwater valves to be installed at sanitary sewer system. Specification section 221319-7-C requires floor clean out tops/deck plates to be installed in floors above backwater valves of interior installation. Backwater valves are shown to be installed at electrical room 002, chemical room 029 and Presidents dining room 014. At room 014, please clarify if a floor cleanout top/deck plate is allowed or if a wall access panel in a plumbing chase or corner of room of sufficient size would be acceptable. | Please clairfy acceptable means of cleanout access for the backwater valve at room 014. | No wall or floor clean out access will be acceptable in President's Dinning 014. All attempts are to be made for access within Restroom 016. |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/24/2020 |  |  |  |  | Closed | 02/27/2020 | 03/05/2020 |  | 03/03/2020 | 02/24/2020
273 |  | 0 | 230000 | M110 | Request for Information | Laundry Dryer Vent Requirement | Drawing M110, Laundry room at grid line AG and A5 is shown a dryer with no means of venting. Is a vent required for this dryer? See attached for clarification. | Please confirm whether venting for this dryer is needed and provide detail if so. | Size of dryer vent is 4”, See CCD28R1. ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/24/2020 |  |  |  |  | Closed | 02/27/2020 | 03/18/2020 | 03/14/2020 | 02/25/2020 | 02/24/2020
274 |  | 0 |  |  | Request for Information | CB-7 at 8" walls at doors AB and AC/ A7 to A8 Annex | Reference sheet S100 and S101A. There are two door openings north of grid A7 around grids AB and AC. The dimension is shown as 8" walls on S100 but on S101A the CB-7 beam headers are 12" wide. It also appears the precast at grid AB should have a 12" wall to set on. Please review and let us know if these should be 12" wide walls/ jambs. |  | The wall just east of Grid AC is an 8" wall. The concrete beam schedule will be updated with an 8" header callout. The wall on Grid AB should be 12" and will be changed to reflect that. These changes will be included in CCD034. ¦ See ARW's response |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/24/2020 |  |  |  |  | Closed | 03/08/2020 | 03/19/2020 | 03/18/2020 | 02/25/2020 | 02/24/2020
275 |  | 0 |  |  | Request for Information | Floor penetrations for BIM coordination | Attached are the locations of several 3 and 4 inch holes we need to put in the pan deck floors in the west tower for electrical conduits. We will be sleeving them before concert is placed so no rebar will be cut, we will also tie an additional bar in the slab around the holes. |  | See comments below ¦ ¦ One point of clarification, the floors are 7" suspended concrete slab floors with rebar 8" o.c. each direction (typical at all levels), no metal deck. With that, Zach will these size and locations still work? ¦ The spacing of the holes is fine provided additional slab reinforcing is provided per detail 11/S201. The holes will likely need to be further from the wall than 3". There are multiple additional slab bars in the slab at the edge. The holes cannot interfere with these bars. See detail 7/S222 for a detail of those additional slab bars. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/25/2020 |  |  |  |  | Closed | 03/03/2020 | 03/03/2020 | 02/28/2020 | 02/26/2020 | 02/25/2020
276 |  | 0 |  |  | Request for Information | Buttress detail 9/S212 | Reference 9/S212 In our meeting with Scott Gillberg on 2/20/20 we discussed RFI 90 and the option to extend the buttress to the footing as referenced on 9/S212. Buttress plinths extended to the footing is also how it is shown on the BIM model. We were asked to put together a rebar shop drawing of how this detail would work. Included on the shop drawing is 3 conditions: suspended slab, east and west continuous footing and full height. Please review attached details and let us know if they will work. With the Westland team it was also determined that by extending the buttress plinth to the footing it would give a better water proofing detail. Also note that we anticipate the new dimension of the buttress as being 24" wide instead of 18" wide. |  | ARW can you confirm the rebar details? It is approved to widen the Buttress Plinth/Footing to 24", this will allow for the 3" chamfer detail to be on all 3 sides of the buttress. ¦ We take no exceptions to what is shown and requested. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/25/2020 |  |  |  |  | Closed | 03/03/2020 | 03/05/2020 |  | 02/26/2020 | 02/25/2020
277 |  | 0 |  |  | Request for Information | Mat Footing Bearing Capacity | Attached is the information for the 110 ton crane. The actual load chart for the crane that will be used is in route from Texas. In speaking with Ross the crane weight in configuration will be around 140,000# + load. We will need to know if this will work setting up on the mat footing for some of our form picks at the annex shear walls. The actual outrigger load will be calculated when the machine arrives with its chart. How many pounds per square foot can safely be placed on the existing "Annex" basement mat slab? |  | See ARW's response ¦ The amount of load that the basement mat slab can support is very dependent on the outrigger layout, loads to each outrigger and where it is located on the mat slab. The contractor will need to provide this information before it can be determined if the slab can support the proposed loads. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/25/2020 |  |  |  |  | Closed | 02/28/2020 | 03/12/2020 | 02/28/2020 | 02/26/2020 | 02/25/2020
278 |  | 0 |  |  | Request for Information | Level 2 Joist Bearing | Please confirm that in order to ensure the existing wood joists that do not bear directly on the new I-beams they will need shims installed under them to insure they bear uniformly. |  | See ARW's response ¦ Yes. Please provide shims as required and refer to detail 7/S221 for general conditions at these beam locations. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/26/2020 |  |  |  |  | Closed | 03/03/2020 | 03/04/2020 | 02/28/2020 | 02/26/2020 | 02/26/2020
279 |  | 0 |  |  | Request for Information | Micropile Questions | There is a note in the structural plans that indicates the permanent casing on the micropiles must go 5' into bedrock. The micropile submittal requires a minimum of 4' into bedrock. Is 4' minimum embedment acceptable. Current micropiles are being installed with 5' of embedment until this question is answered. A reference in the specification section 316330 sub section 3.3.D.5 is made to a proof testing frequency of 25% unless otherwise defined. The micropile designer (Gordon Geotechnical) has required 5% in his design. Production testing of 5% is industry standard and is what has been required in the approved micropile submittal. Please confirm 5% is acceptable. |  | ¦ Please continue to use the 5' minimum permanent casing embedment. 5% proof testing is acceptable. The 25% requirement in the spec section was a typo and will be revised. |  |  | High | Matt Madsen | Malcolm Drilling Co Inc | CRSA ARCHITECTURE |  | 02/26/2020 |  |  |  |  | Closed | 02/29/2020 | 03/05/2020 |  | 03/05/2020 | 02/26/2020
280 |  | 0 |  | AD 102 | Request for Information | Level 2 Sub-floor | On Sheet AD 102 the flooring being demoed calls out note 2.87, see note below. In addition to the Carpet there is some 1\4” MDF that has been installed, see photo attached. Please advise if this needs to be removed. |  | Please see upcoming CCD-11-R.5 for the sub-floor removal. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/26/2020 |  |  |  |  | Closed | 02/29/2020 | 02/27/2020 | 02/27/2020 |  | 02/26/2020
281 |  | 0 |  |  | Request for Information | Quatrefoil Columns Level 2 Historical | There is not enough room to reuse existing quatrefoil columns at Lobby rm 218 once existing structure columns are wrapped with metal and carbon fiber wrap. See attached photo looking down at existing structure column and quatrefoil columns. I believe this will be the same condition at all columns. Demo drawings say to reuse these columns. I believe course of action is to make new columns larger in diameter. Please specify course of action for these quatrefoil columns. Quatrefoil capitals to be made to match existing will all be different shape in diameter to due existing quatrefoil columns not be the same size in diameter. This will be near impossible to due to irregularity in size. | Suggestion is to make all new quatrefoil columns and capitals. Size of columns will very at Lobby rm 218 and may very at instruction rooms. Columns front of instruction room to remain size as shown | This has been discussed with the client and the resolution is still to be determined. This will be part of an upcoming CCD-19. ¦ |  |  | High | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 02/27/2020 |  |  |  |  | Closed | 03/01/2020 | 03/12/2020 | 03/06/2020 | 02/27/2020 | 02/27/2020
282 |  | 0 |  |  | Request for Information | Cross tie size confirmation detail 10/S240 | Reference cross tie detail 10/S240 Per discussion between Zach Hansen ARW and Judd Bundy Innovative concrete on 2/27/20. Please confirm that the cross tie for the concrete infill's referenced on detail 10/S240 is #4 bar. We used #6 at some locations not knowing the size we assume this is ok. |  | This is acceptable. A #4 tie is adequate for this and has been clarified in forthcoming CCD 034 |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 02/27/2020 |  |  |  |  | Closed | 03/05/2020 | 03/05/2020 |  | 03/05/2020 | 02/27/2020
283 |  | 0 |  |  | Request for Information | Single Tree Removal on East side | This is an RFI to confirm that the tree called out on the attachment can now be removed per owner direction. |  | There is concern about general heath and safety issues this tree poses as it continues to grow at an angle and lean to the east and over the adjacent sidewalk. Due to these safety concerns the owner has requested that the tree called out in the attachment is removed. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Landscape Architects |  | 02/28/2020 |  |  |  |  | Closed |  | 03/12/2020 | 03/06/2020 | 03/02/2020 | 02/28/2020
284 |  | 0 |  | S100A | Request for Information | Interior Pile off Set from Stone Column | Will you please confirm that per a phone conversation between David Adams, Carter Cluff, Dion Graybill, and Zack Hansen on Friday 2-28 that the Center lines for the Piles on the interior footings are to be 1 ½” off the Face of the Stone Column as shown below. This will allow for the C- channel that has a 3” top and bottom leg to be centered on the pile instead of being 1 ½” off center as shown below. |  | Please see Zach Hansen's Confirmation. ¦ ¦ This is correct. We take no exception to the dimensions outlined. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/02/2020 |  |  |  |  | Closed | 03/05/2020 | 03/04/2020 | 03/02/2020 | 03/02/2020 | 03/02/2020
285 |  | 0 |  |  | Request for Information | Carbon Fiber Stone Column Wrap | Per a conversation had on 3-2-20 between David Adams, Dion Graybill and Zack Hansen Please confirm that this vertical section of the historic wood truss can be removed, have the fiber reinforcing installed, then the wood block is to be reinstalled. this will allow for the Carbon Fiber to be installed directly to the Stone column, and would allow for the Steel support to be installed as well. |  | See Response from Zach Hansen - ARW. ¦ ¦ We concur and take no issue with what is described. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/02/2020 |  |  |  |  | Closed | 03/05/2020 | 03/04/2020 | 03/02/2020 | 03/02/2020 | 03/02/2020
286 |  | 0 |  |  | Request for Information | Tower fire alarm | This question arose when reviewing the existing condition of the tower having 4 sensors one on each level. The drawings (both Envisions and our FA sub. AAA) show 1 heat detector on the ceiling of the large room at the bottom of the tower. Is this going to be adequate coverage please advise. |  | Please provide 4 heat detectors in tower, one per level similar to existing conditions. ¦ See response from Jessica with Envision. Provide Heat Detectors at each level. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/03/2020 |  |  |  |  | Closed | 03/10/2020 | 03/19/2020 | 03/18/2020 | 03/05/2020 | 03/03/2020
287 |  | 0 |  |  | Request for Information | Soda Line Pull Box | On Sheet QF301 under Electrical Notes #10 it calls for a pull box every 50’. Even with a straight line it will would be 66’. | If it's necessary please provide a location. | See PKC's response. Pull box location has been indicated. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/03/2020 |  |  |  |  | Closed | 03/10/2020 | 03/19/2020 | 03/19/2020 |  | 03/03/2020
288 |  | 0 |  |  | Request for Information | Schonbek: Family B - Cast Arm Design | At the meeting on Feb. 19th Gloria and Josh showed a "sawtooth" pattern for the Family B cast metal arm. Attached there's an image of a stepped "sawtooth" and a "triangle" pattern. Are either of these desirable? If not, please send a drawing of the pattern you'd like and also where it should be located on the arm. Thank you! (attachments) |  | We have already addressed everything in recent meeting in St. George. ¦ Questions were resolved in a deco lighting design meeting. ¦ ¦ ¦ Please provide what the resolutions where that resulted from the St. George Meeting |  |  | Medium | Claudia Hawkins | Swarovski Lighting Ltd. | Interior Designer |  | 03/04/2020 |  |  |  |  | Closed | 03/10/2020 | 08/20/2020 | 08/20/2020 | 04/29/2020 | 03/03/2020
289 |  | 0 |  |  | Request for Information | Flooring Details | We are ordering the electrical floor boxes and need flooring details and the architect to select the colors for the covers. We need details for the following floor types. FS1, FS2,FC6,FC7,FW1 and FW2 |  |  |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/03/2020 |  |  |  |  | Closed | 03/10/2020 | 03/12/2020 |  | 03/12/2020 | 03/03/2020
290 |  | 0 |  |  | Request for Information | Paving Submittal Return |  |  | Bob I attached this RFI to the paver submittal and sent it in again for a new review. We'll track it there. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Westland PE’s |  | 03/03/2020 |  |  |  |  | Closed | 03/10/2020 | 03/05/2020 | 03/05/2020 |  | 03/03/2020
291 |  | 0 |  |  | Request for Information | Annex grid AH wall cap dowels embedment | Please confirm that along grid AH at annex we have two locations above door headers where we cannot drill 19" for embedment. The holes we have drilled reached 15" before hitting something solid. Please verify if these are acceptable at 15" or provide options. This was reviewed onsite with ARW on 2/28 |  | See response from ARW. ¦ ¦ ¦ Each U-bar that is drilled with 15" embedment will need to have an additional u-bar installed in the wall within 6" of the adjacent ubar. It is acceptable for this additional u-bar to have 15" embedment. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 03/06/2020 |  |  |  |  | Closed | 03/12/2020 | 03/19/2020 | 03/17/2020 | 03/12/2020 | 03/06/2020
292 |  | 0 |  |  | Request for Information | Annex mat footing bulkhead | At grid A10 midpoint between AD and AE would it be acceptable to put a bulkhead in the mat footing at the location marked on the attached plan. With current phase of construction there is a ramp that will be needed for equipment access. We would add waterstop top and bottom (similar to 13/S210) and have rebar dowel out per lap splice requirement. This is a means and methods but want to make sure it will not be an issue with structural. |  | We take no issue with this method. Please connect the separate pours with rebar lap splices as noted in the drawings. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 03/06/2020 |  |  |  |  | Closed | 03/13/2020 | 03/19/2020 | 03/12/2020 | 03/16/2020 | 03/06/2020
293 |  | 0 |  |  | Request for Information | Level 5 Duct Penetrations | Please confirm that per a conversation between David Adams, Jason Fullmer, and Zach Hanson on 3-06-2020. That it is acceptable to use Detail 8/S240 on the Duct penetrations going through the stone wall separating the historical building and the new stair tower on level 5. The structural fix for these penetrations is that we will install shoring under the roof purlins so they can be cut at the stone wall. Then cut the opening in accordance with Detail 8 on sheet S240 with a 1’ cut on the top of the opening extending into the stone to hold a 1/2” plate used to support the opening until it can be filled in with the concrete. Once it has been infilled, we will install a Simpson HGUM saddle to carry the roof purlin. On all of the circular opening we will follow Detail 7 on Sheet S240. |  | Confirmed |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/06/2020 |  |  |  |  | Closed | 03/09/2020 | 03/09/2020 | 03/06/2020 |  | 03/06/2020
294 |  | 0 | 220000 | P502 | Request for Information | Epoxy coating requirements at vaults | Per an on-site conversation with VBFA on 3-5-20, epoxy coating requirements for all below grade vaults was discussed. No specification or detail is currently provided indicating these epoxy requirements. | Please provide specification of epoxy coating to be applied at below grade vaults as found on drawing P502 attached. | please see response from VBFA ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/09/2020 |  |  |  |  | Closed | 03/16/2020 | 04/14/2020 | 04/10/2020 | 04/10/2020 | 03/09/2020
295 |  | 0 |  |  | Request for Information | Joint filler material | Please confirm joint filler material for fountain coping, seat wall caps and planter caps. Detail 6/LL508 shows a mortar joint under the cap but there is no reference to the stone to stone joints. | With the use of darker stone and the wide thermal swings for the area a mortar joint will undoubtably crack. We would suggest that a silicone sealant be used for all stone joints to allow for expansion and contraction. | A silicon sealtant is acceptable for all stone joints. Provide product data and color samples for review. ¦ ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 03/09/2020 |  |  |  |  | Closed | 03/16/2020 | 03/30/2020 | 03/30/2020 | 03/27/2020 | 03/09/2020
296 |  | 0 | 220529,230529 | M504 | Request for Information | Historic wood joist angle support attachment | Following an on-site discussion with VBFA regarding supports at Historic wood joists. Specification section 230529-9 K building attachments #13 and specification section 220529-9 I building attachments #13 both indicate to install MSS type 34 "Angle Clips" to be used to hang/support hydronic and plumbing piping from wood joists. This appears to be the only attachment method approved for hanger systems at wood joists located within the historic structure. Drawing M504, detail 6 appears to show the only acceptable method of fastening angle clips with a thru bolt drilled through the wood joist. See attached photo of level 5 wood beams that are 6" wide and thru bolted per the detail with angle clip attached. Although this type of support and installation will be superior for heavy loads of pipe (Possibly 3" and larger), it might be somewhat excessive for small diameter pipe and lighter loads. Please see attached cut sheets for the "Sammy" side and bottom attachments for reference to support options for these lighter loads. Please advise if the attached "Sammy" support material, grabber screw or other alternative means of support using the angle clips is an approved method. |  | DEWALT® Hangermate Anchors,"Sammy", is an approved method to use. ¦ Structurally, the Sammy connection is okay to be installed in the wood joist provided that a hole is predrilled into the wood joist to prevent the joist from splitting when the Sammy hanger is installed. Loads suspended from the Sammy hanger may not exceed 75lbs and each floor joist is allowed to only have one hanger installed. If conditions require a different condition, then please notify the architect and engineer so a solution can be determined. |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/10/2020 |  |  |  |  | Closed | 03/14/2020 | 03/26/2020 | 03/23/2020 | 03/11/2020 | 03/10/2020
297 |  | 0 |  | AE4508, EL105B | Request for Information | Lighting 5th floor North and South stair towers | There are no lights shown on drawings at 5th floor North and South stair towers (see attached drawings) please advise. |  | See response from Envision. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/10/2020 |  |  |  |  | Closed | 03/17/2020 | 04/15/2020 | 04/13/2020 | 03/11/2020 | 03/10/2020
298 |  | 0 |  |  | Request for Information | Steel Continuation at Columns - Level 3 | Please provide further information regarding the column to column connection (ref 8/S244). Currently this connection does not appear to take into account the wood beam at level 3, or the lattice truce that extends behind this connection. |  | The new steel columns are to be installed to the bottom side of the floor beams. This is the same as we discussed during our meeting between Glassy, ARW and Westland last week. We will add clarification to details 8/S244 and 2/S246 to show the columns extending to the underside of the floor framing. This clarification will be added to CCD037-R.1 ¦ ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 03/11/2020 |  |  |  |  | Closed | 03/18/2020 | 03/30/2020 | 03/19/2020 | 03/18/2020 | 03/11/2020
299 |  | 0 |  |  | Request for Information | CCD 006r2 Pavers | Sheet C.6, Key note #24 calls for a vehicular paver at the crossing of 400 South and also at the crossing at 300 East. The drawing is unclear of the extent of pavers and what color. The Key note references Sheet LL501 which references the plans. Please clarify this information for pricing. |  | The finish of these two pedestrian crossings is to be scored concrete. See sheets LL101 and LL106 for score joint layout. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 03/11/2020 |  |  |  |  | Closed | 03/18/2020 | 03/23/2020 | 03/18/2020 | 03/18/2020 | 03/11/2020
300 |  | 0 |  |  | Request for Information | Radius Ceiling Information - Instruction Room below Level 4 | Please provide specific information regarding radius, elevation, etc in reference to the ceiling. GSW is modeling the support steel for this ceiling and we are unable to determine control, etc. |  | It is crucial that this ceiling be field verified. The rolled HSS tube is to match the curvature of the bottom chord of the wooden truss. The overall shape is to be 1/2 of an ellipse where width apex occurs where the truss meets the wall and height apex is bottom of wooden truss at its center point. I have provided a few dimensions for reference, but these really do need to be field verified. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 03/11/2020 |  |  |  |  | Closed | 03/18/2020 | 04/09/2020 | 04/01/2020 | 03/12/2020 | 03/11/2020
301 |  | 0 | 230000 | CCD#028 M100, M106 | Request for Information | CCD#028-Dryer Duct | CCD#028, drawing M100, paragraph 3 and M106 paragraph 1 reads to provide new dryer exhaust ducting. No size appears to be indicated for this ducting. The duct system also appears to exceed 35' in length which is the maximum length allowed without the use of a booster fan and lint trap per typical code requirements. Please provide dryer vent duct sizing and advise if a booster fan and lint trap are to be installed/required. If so, provide booster fan and lint trap schedule/info/spec. |  | The dryer duct size should be 4" A Fantech booster fan will be added with a lint trap via CCD28 revision. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/11/2020 |  |  |  |  | Closed | 03/18/2020 | 03/19/2020 | 03/18/2020 | 03/18/2020 | 03/11/2020
302 |  | 0 | 230000 | M100A, M100B | Request for Information | M100A, M100B Missing Duct and Grill sizes | Drawing M100A, gridline H2 and H1 and HC to HB are two (2) ducts rising to the floor of level 1 with no sizes shown. Drawing M100B at same location there are two (2) floor registers with no sizes shown. | Please advise as to what the duct and register sizes are to be...see attached drawing snapshots for clarification. | Grilles and ducts are 32/6. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/11/2020 |  |  |  |  | Closed | 03/18/2020 | 03/18/2020 | 03/18/2020 | 03/16/2020 | 03/11/2020
303 |  | 0 |  |  | Request for Information | Sump Vault Switch Conformation | Please confirm that the sump vaults in the Mat Slab of the North Addition (SP 5A, 5B & SP 2A, 2B) are to switch from precast to cast-in-place concrete. I attached an email from ARW where we were given the reinforcement for the concrete. |  | This is correct, Precast vault has changed to cast-in-place concrete per ARW's markup. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/12/2020 |  |  |  |  | Closed | 03/15/2020 | 03/19/2020 | 03/18/2020 |  | 03/12/2020
304 |  | 0 | 220000 | P-099, P-110 | Request for Information | FS-1, FD-2 at Annex Mechanical Room | Drawing P-099, North Mechanical Room 001, keynote 5 indicates a floor drain FD-2 to be installed at north wall, see marked up drawing attached. Drawing P-110 indicates a floor sink FS-1 at this same location. Based upon sewer inverts given for gravity sewer leaving the building, BIM coordination has determined the floor sink needed to accept backwash from the fountain equipment would need to be installed 5 3/4" above FFE at this location indicated. An emergency eyewash is also shown in this area and would appear to be drained by the shown FD-2. It appears that both the FS-1 and FD-2 fixtures are needed in this mechanical room. | Please confirm both drainage fixtures FS-1 and FD-2 are desired to be located in mechanical room 001. If so, confirm installing FS-1 floor sink at an elevation with concrete curb is acceptable similar to detail 1, WF-400 attached. | Please see CCD-29 per VBFA's comment. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/12/2020 |  |  |  |  | Closed | 03/19/2020 | 03/19/2020 | 03/19/2020 | 03/18/2020 | 03/12/2020
305 |  | 0 |  | AE4007, AE577 | Request for Information | Laundry Room 028 Casework AE4007 | Cross Section C4/AE577 calls for uppers and lowers in the Laundry Room to be p-lam casework. Cross Sections C1, C2, C3, /AE577 calls for full height casework in the Laundry Room to be stained grade veneer. Which is correct p-lam or stained grade casework? I have never seen stained grade in a laundry room temple before and would assume that this casework is to be p-lam. |  | P-lam only in the Laundry Room. Note has been updated. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 03/13/2020 |  |  |  |  | Closed | 03/20/2020 | 04/09/2020 | 04/01/2020 | 03/17/2020 | 03/13/2020
306 |  | 0 |  |  | Request for Information | CCD 041 sheet AE146 clarification | Reference attached mark ups on sheet AE146 Please clarify the following: 1) Where the shop ramp is at grid AH/ A4-A3 will the stem walls for the slab step be CW-2 type walls or CW-1? Structural sheet not provided reflecting this. Arch shows 6" 2) At grid AH between A2 to A5.3 the wall that is capped is shown as face of wall 10 3/4" from grid AH. This does not appear correct when referencing the AP101 drawing and AE147 drawing. Our understanding is the outside face of concrete should have a 3" chamfer dimensioned from the face of precast. We assume AP101 is the correct precast dimension and we should add 3" to this for wall concrete. The haunch/ buttress dimensions are different. 3) Dimensions to TD1 trench see S100 and M100 4) Clarify elevator pit elevation. Reference RFI 263 5) Verify if all slab on grade recesses not shown on structural to be detailed per 4/S203 6) Clarify freezer pad elevation and structural detail 3/S210 7) Provide missing buttress dimensions marked on plan 8) Are the area well drains at elevation 87'-0"? See markup |  | 1) We anticipated that the ramp would be poured as a solid ramp since it is only 2feet tall. If it is desired to use fill and stem walls, then a 6” concrete wall (CW-1) can be used. 2) Not answered by ARW 3) Not answered by ARW 4) According to as-built drawings, this is an existing elevator pit that is recessed into the existing mat slab 1’-6” which would put the elevation of the pit at 83’-6”. Field verify the actual condition. 5) Yes, all slab on grade recesses to be per 4/S203 unless noted otherwise. 6) The 86’-2” is the elevation of the top of the recessed slab. There will then be insulation and a topping slab placed on top of that (see 3/S210) to bring the floor slab up to elevation 87’-0”. 7) Not answered by ARW ¦ please see answers provided by crsa and arw. also reference ASI #13 ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 03/16/2020 |  |  |  |  | Closed | 03/26/2020 | 03/24/2020 | 03/24/2020 | 03/19/2020 | 03/16/2020
307 |  | 0 |  |  | Request for Information | East Fountain Geometry | The east fountain geometry is not working with the details on Sheet LL506 & LL508. See attached sheets. Sheet LL506 Please verify the dimension from inside corner at radius to outside face of precast. The 5’ 10 dimension does not match with the 7’ 0 radius Sheet LL508 Detail 9 is referred to for both decorative corner cap and typical cap. Both have different profiles but only one is dimensioned and provided on 9/LL508. It does not match the decorative cap and is too thick to match the typical stone cap at 3”. Please clarify Decorative corner cap is dimensioned at 2’ 2 detail 10, but dimensioned at 2’4 on detail 2. Please clarify |  | See attached for updated sheets LL506 and LL508. LL506 - Proceed with holding to the 7'-0" radius dimension. LL508 - The corner cap is 2'-4" square, see updated sheet. The corner caps are intended to be 6" thick, with the bottom 3" matching the profile of the 3" thick cap on the rest of the fountain walls. ¦ ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 03/17/2020 |  |  |  |  | Closed | 03/24/2020 | 03/25/2020 | 03/25/2020 | 03/18/2020 | 03/17/2020
308 |  | 0 |  | EP105 | Request for Information | 5th floor outlets | can we relocate outlets in hallway 516 to match outlets in hallway 520? With this change we would not need to remove as much historical plaster. |  | We have no issue with relocating outlets to make installation easier. Contractor to confirm the items below and coordinate exact locations with the architect/interior designer for exact placement. Outlets locations typically should avoid being back to back to prevent sound transfer and also if walls are fire rated, to maintain integrity of the fire rating of the wall. I don’t think any of those walls are fire rated though. Outlets should be located per arch’l elevations to align with lamps, furniture, wall finishes, etc. CRSA should double check these prior to final direction to contractor. The back to back outlets on the one side, may need to shifted slightly to avoid boxes being directly behind one another. ¦ CRSA concurs with response from ELec engineer. THe lights indicated in the pdf from elec sub my be relocated as suggested. any elec outlets on walls where furniture is present need to be located as shown in enlarged elevations. ¦ Please provide layout associated with the placement of the electrical outlets. ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/09/2020 |  |  |  |  | Closed | 03/24/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020 | 03/17/2020
309 |  | 0 |  |  | Request for Information | Room layout Consistency | Instruction room outlets switches and t-stats are not shown consistently on details. Should we follow details or install consistently? please advise |  | Install consistently. Outlet, switches, t-stats (any device stacked vertically) should all align where possible. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/17/2020 |  |  |  |  | Closed | 03/24/2020 | 03/19/2020 | 03/18/2020 | 03/18/2020 | 03/17/2020
310 |  | 0 | 220000 | P-009, AE 140 | Request for Information | In wall cleanouts at annex kitchen | Drawing P-009 indicates 3(Three) 4" in-wall cleanouts rising out of slab adjacent to concrete bearing wall at north side of annex basement kitchen. See attached red-lined drawing P-009 for reference. Drawing AE 140 indicates the wall type at this location to be type 13, 3 5/8 steel stud wall furred at concrete wall. See attached AE 140 drawing for reference. We have attached a BIM model screen shot for reference and reveiw. As currently designed and drawn, the 3 5/8" steel stud wall will not have enough spacing to allow for the install of the 4" round vents at this location. | Please provide a revision to wall type or routing of vents to new location so as to allow the vents enough spacing to be installed within wall. | See VBFA's response ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/18/2020 |  |  |  |  | Closed | 03/25/2020 | 04/01/2020 | 04/01/2020 | 03/18/2020 | 03/18/2020
311 |  | 0 | 230000 | M101 | Request for Information | Annex level 1 missing duct and register sizes | Drawing M101, annex level 1 upon review it appears there are various ducts and registers missing sizes. They are as follows: Between gridlines HD to AB and below A5 there are two (2) missing register and duct size callouts. Between gridlines AC to HD above A4 there is a missing duct and register size callout. Along gridline AF and above A4 there are two (2) missing register callouts. Along gridline AC and below A3 there are four (4) missing register callouts. | Please provide the missing dimensions for both duct and registers as indicated. | All various ducts and registers that had missing sizes have been corrected, see forthcoming CCD. ¦ Please provide the CCD #. ¦ ¦ ¦ Please provide the CCD # |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/18/2020 |  |  |  |  | Closed | 03/25/2020 | 04/01/2020 | 04/01/2020 | 03/23/2020 | 03/18/2020
312 |  | 0 |  |  | Request for Information | Light fixtures at medallions | Is there a detail that shows how the structure, ceiling system, medallion and light fixtures work together |  | This detail is still in the works as we progress through design with the lighting designer. more information to be provided asap. ¦ Please see CCD - 019R.5 showing revised details. |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 08/25/2020 |  |  |  |  | Closed | 09/20/2020 | 01/13/2021 | 01/04/2021 | 03/24/2020 | 03/18/2020
313 |  | 0 | 230000 | M103, AE123 | Request for Information | Electrical Room 315 duct | Drawing M103, electrical room 315, indicates a lined return duct at 32" x 14". Ceiling space from floor joists of level 4 to to finish ceiling of level 3 is only 12". The duct installed will end up 2" below ceiling per reflected ceiling plan on drawing AE123. See attached clouded drawings for reference. | Suggest re-sizing of duct or lowering of ceiling at this location. | ¦ The return duct will be moved additional 12” towards the center of the room away from the transom window. See forthcoming ASI #12 for more infomation. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/20/2020 |  |  |  |  | Closed | 03/27/2020 | 03/30/2020 | 03/30/2020 | 03/27/2020 | 03/20/2020
314 |  | 0 | 321313 |  | Request for Information | Landscape Concrete Conformation | Per the mock up review with Chris Robbins onsite last week. Please confirm that the landscape concrete will be a medium broom finish with the original approved mix design submitted in January (321313.01). Note: this original submittal did not include any of the tan aggregates or pea gravel. |  | medium broom finish was agreed to be design team and ownership. tan aggregate not needed as aggregate will not be visible. submittal has previously been reviewed and approved. please proceed. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/23/2020 |  |  |  |  | Closed | 03/30/2020 | 04/01/2020 | 03/27/2020 |  | 03/23/2020
315 |  | 0 |  |  | Request for Information | Soda Line Pull Box Type | What pull box is wanted for the soda lines referenced in note 10 of Electrical Notes on sheet QF301? |  | See attached response from PKC |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/23/2020 |  |  |  |  | Closed | 03/30/2020 | 03/27/2020 | 03/27/2020 | 03/26/2020 | 03/23/2020
316 |  | 0 |  |  | Request for Information | Level 5 Ducting Penetrations | Please confirm that the section highlighted in yellow in the attached document can be cut out and the remaining section not filled by ducting can be poured back in with concrete. The framing members effected will be shored up while the ducting is placed and the concrete is formed and poured. Please provide the detail we discussed showing the reinforcement and spacing along with the hangers needed. |  | See attached for ARW markups in GREEN. ¦ Please see response from ARW. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Judd Bundy | Innovative Concrete LLC | 03/23/2020 |  |  |  |  | Closed | 03/26/2020 | 03/30/2020 | 03/27/2020 | 03/30/2020 | 03/23/2020
317 |  | 0 |  |  | Request for Information | Fireproofing of Steel in Annex | As far as we can tell all steel in the Annex will be fireproofed. We intend to leave our steel uncoated in order to receive fireproofing product. Currently the joists are coated with primer paint (dip coat), but steel columns, beams, angles & channels are figured as "no paint". Please confirm all steel (floor & roof) will be fireproofed. |  | Westland to inquire with their Fireproofing contractor to verify what is acceptable. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 03/23/2020 |  |  |  |  | Closed | 03/30/2020 | 04/09/2020 | 04/03/2020 | 03/24/2020 | 03/23/2020
318 |  | 0 |  |  | Request for Information | Galvanized Font Level Steel | Details 1 & 2 on sheet S241 include a "sloping" portion of the stone columns / walls which are to be wrapped in concrete. At what point will these slopes be able to be determined? GSW intends to get the steel into fabrication for this area asap and will need this information in order to achieve accurate dimensions for our steel prior to galvanizing. |  | Please field measure when you are on site. |  |  | Medium | Brett Glassey | Glassey Steel Works | Westland PE’s |  | 03/24/2020 |  |  |  |  | Closed | 03/30/2020 | 06/10/2020 | 06/10/2020 |  | 03/24/2020
319 |  | 0 |  |  | Request for Information | Arborist's Recomendation for Pre-existing tree conditions | The Arborist’s Initial Tree Report provided the following recommendations for the trees on the projects, having to do with the pre-existing conditions of the trees. This report was previously forwarded to Westland, and we continue to await instructions. The recommendations are as follows: 1. The ash trees along 400 South are recommended for removal for the following reasons: a. They are root bound and have girdling roots b. The feeder roots are rotting c. All the trees show signs of termites (causing the trees to become hazardous) d. They have been over pruned for years weakening the branches e. Large branches are dying, bark sloughing off and cracking (hazardous) f. Borer damage g. Not enough soil space for the roots The Arborist has indicated “that these trees must be removed and cannot be saved” because the “damage is too severe”. 2. The Deador Cedar tree in the northwest corner of the property required treatment with a fungicide and pesticide, along with a deep root feeding of micronutrients and iron. We directed him to perform this treatment, as it was sensitive to the seasonal temperatures and growing season, but had minimal cost. 3. The Mulberry tree that has been cabled, needs to be cabled and braced before leaves come on, to ANSI standards by a certified arborist. Each of these three recommendations require direction from the owner to complete since they were not included in the contract scope, and thus there is additional cost associated with this work. Please advise how we are to proceed. |  | The tasks listed will need to have final owner review and approval prior to starting work. 400 S work is still being determined in the plans as well as the actual ownership documentation. Please stand by for additional information and direction. ¦ Pricing has been forwarded to Church PM. Please standby for additional direction. ¦ Owner has denied tree removal Has been completed by other parties Has been completed by other parties ¦ ¦ Attached please find the pricing proposal for the Arborist to perform the cabling of the Mulberry tree #57, per item #3 in this RFI. ¦ Please provide an update when it is given by the Owner. |  |  | High | Tim Maynes | Stratton & Bratt Landscaping | Landscape Architects |  | 03/24/2020 |  |  |  |  | Closed | 04/01/2020 | 06/10/2020 | 06/10/2020 | 03/27/2020 | 03/24/2020
320 |  | 0 |  |  | Request for Information | Missing Sheet AE608 | On sheet AE632 detail D3 it references detail C1 on sheet AE608. We can’t find sheet AE608, is this a sheet we need to see or does this note need to be changed? Please advise. I have attached the note from sheet AE632 for reference. |  | Detail reference should refer to A1/AE633. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/24/2020 |  |  |  |  | Closed | 03/31/2020 | 04/01/2020 | 03/31/2020 |  | 03/24/2020
321 |  | 0 |  |  | Request for Information | CCD 41r1 Slab elevations | Sheet A147 denotes slab elevation changes North of grid A7. This change appears to be accomplished by lowering the top of steel elevation to 99'-3-1/2". South of the wall, however, there is a depressed slab elevation between AE & AF that is also called out as 99'-8". In this specific area - the top of steel is at 99'-5-1/2". This would only provide 2.5" of concrete - deck included. Is this the correct elevation for this slab depression? If so - please provide direction as to top of steel in this area. Also - in the area requiring 8.5" of concrete - is the deck gauge affected? |  | The recessed slab elevations will be addressed by the architect. The 8.5" slab deck is required to be shored per note 16 on sheet S101A. If the contractor desires to provide a heavier gauge deck that won't require shoring please submit this for review and approval. ¦ Recessed Slab North of A8 (Entry) is to be at 99'-8" Recessed Slabs South of A8 (Tiled areas) are to be at 99'-10" A revised AE147 is attached and will be sent to the Contractor as part of CCD-041.R3 ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/01/2020 | 04/07/2020 | 04/01/2020 | 03/25/2020 | 03/25/2020
322 |  | 0 | 085200 | AE645 | Request for Information | Glazing Clarifications | Item #1: On Sheet AE645 in the upper right-hand corner Glazing Note D is described as TEMPERED ART GLASS – ¾” TRIPLE PANE IGU “WHITE OVPAL SWIRLED, SEE APPROVED SAMPLE. This glass is scheduled for Window Type H12 – Qty: 5 Openings 116 – 120 on the 0.5 Floor Plan Level – North Elevation. Please provide information on manufacturer of glass or where a glass sample can be obtained. |  | See CCD-101 - Door and Window clarifications. ¦ |  |  | Medium | Todd Maxwell | Re-View Windows, Inc. | Interior Designer |  | 03/25/2020 |  |  |  |  | Closed | 04/03/2020 | 12/17/2020 | 12/16/2020 | 04/01/2020 | 03/25/2020
323 |  | 0 |  |  | Request for Information | Demo. Plaster for Electrical Rough | Please confirm that it is acceptable to remove the wall plaster at the interior side of the sealing/instruction rooms from the door frame to the east perpendicular wall. This is to provide access for electrical roughin. Typical for sealing and instruction rooms on level 5 and 3. |  | This is part of CCD-11-R.2 ¦ Correction. Refer to CCD-11-R.8. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Kyle Welch | CRSA ARCHITECTURE | 03/25/2020 |  |  |  | 3000.00 | Closed | 04/01/2020 | 04/07/2020 | 04/02/2020 | 04/02/2020 | 03/25/2020
324 |  | 0 |  |  | Request for Information | Annex round high windows | Please clarify the following: 1) What elevation are the round windows in the waiting room 109 shown on sheets AE4105, S301 (details A,B,C)? The building sections on AE310 appear that they center @ elevation 120'-6" 2) What is the concrete rough opening dimension and radius for these round windows? I am unsure which details apply to these windows on sheet AE640. The window details reference precast or framed. 3) On AE4105 and AE141 we assume the round window centers above the door in the waiting room and equally spaced as shown between the pillars. This is around 9'-3" spacing. Please confirm this is the correct layout assumption? |  | See attached image of Room 109 showing center of window dimension at 20'-4" above elevation 100. The R.O. diameter size needs to be 2'-9 1/2". The diameter of the Annex high-bay windows itself are 2'-8 1/2". This provides an extra 1 inch for installation. The details would be similar to the details for the West stair tower on sheet AE651. 3. The round windows are centered above the door in the waiting room and equally spaced between pillars at 9'-3" spacing. (See attached image). ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 03/25/2020 |  |  |  |  | Closed | 04/01/2020 | 04/22/2020 | 04/22/2020 | 03/25/2020 | 03/25/2020
325 |  | 0 |  |  | Request for Information | North Stone Column Infills | We had some questions come up on the north columns. There are some areas that need some infilling done and we want to make sure we are doing it in a way that you would like. There are also some places that the wood beams have been cut flush with the side of the column and we want to know if infilling will be needed in these locations. For reference I have attached a PDF version of some photos I took on site. | Please confirm - The column will need to be built back out with grout to the shape of the original column. No reinforcing will be required in the grout since the frp and steel column will be confining the grout at this location. The existing wood will need to be removed from the column and then grouted solid. | This is correct. ¦ ¦ ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Dave Andreas | CDC Restoration & Construction | 03/26/2020 |  |  | 2000.00 |  | Closed | 04/02/2020 | 03/26/2020 | 03/26/2020 | 03/26/2020 | 03/26/2020
326 |  | 0 | 230000 | M103, AE 123, AE662, AE570 | Request for Information | Room 317, 319 SWS Grille installation | Drawing M103, room 317 and 319 indicate a SWS-1 grille, size 18"x 8" to be installed at wall near ceiling. Drawing AE123 indicates a 9' 2 1/2" ceiling height. Top of existing door molding is 8' 4 1/2". Drawing AE662, finish schedule indicates a crown molding to be installed per detail E4/AE570. Per this detail the crown molding is to be 5 1/8" in height. This would appear to only leave a remaining vertical space between top of door frame molding to base of crown molding of 4 7/8". The SWS-1 grille is 8" in height. See attached drawings for reference. Please advise. | Recommend change of grille to a ceiling mount CD as there appears to be enough existing space to allow for install of needed duct and grille. | See response from VBFA. This will be in the upcoming CCD-52. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/26/2020 |  |  |  |  | Closed | 04/02/2020 | 05/11/2020 | 05/06/2020 | 05/06/2020 | 03/26/2020
327 |  | 0 | 230000 | M102, GI202 | Request for Information | Elevator 5 shaft fire damper requirements | Drawing M102, elevator 5 at vestibule 223 is shown 12"x6" duct for both supply and return at the top of the shaft. Drawing GI202 indicates the shaft assembly to be 1 hour rated. Do the supply and return ducts need to include fire smoke dampers? | Please confirm if the supply and return ducts should include FSD's at the top of elevator shaft 5. | Fire smoke dampers are not needed. Install fire dampers at the penetrations into the elevator shaft. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/26/2020 |  |  |  |  | Closed | 04/02/2020 | 04/07/2020 | 04/06/2020 | 04/01/2020 | 03/26/2020
328 |  | 0 | 230000 | M103, S103 | Request for Information | Electrical Room 315 Return Duct opening | Drawing M103, electrical room 315 is shown return duct 28"x12" (30"x14" insulated) rising up through floor of room. Structural Drawing S103 at this same location does not appear to indicate any penetration for the duct work. See attached drawings for reference. | Please provide framing detail for penetration serving this duct work as shown. | Please provide framing for this penetration that is similar to the framing for the penetration on Level 2 directly below this area. We will revise the drawings to show this requirement and issue in a forthcoming CCD 045. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/26/2020 |  |  |  |  | Closed | 04/02/2020 | 04/14/2020 | 04/02/2020 | 03/30/2020 | 03/26/2020
329 |  | 0 |  |  | Request for Information | Curb Wall by Ramp in North Addition | See the attached sketch of a clarification detail for the curb wall by the ramp in the north addition. This was discussed in a meeting between Innovative and Scott. |  | please provide a curb as in detail provided by contractor. curb to be 4" tall and a 6" wide. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/27/2020 |  |  |  |  | Closed | 04/03/2020 | 05/05/2020 | 05/01/2020 |  | 03/27/2020
330 |  | 0 | 262726 |  | Request for Information | Color Selection of wiring devices and wall sensors | See attached occupancy sensor submittal and select color for wall controllers. This color selection also applies to all wiring devices, switches, receptacles, etc. |  | This has already been answered. color shall be matte white finish with a screw-less face plate. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/27/2020 |  |  |  |  | Closed | 04/03/2020 | 04/07/2020 | 04/02/2020 | 03/30/2020 | 03/27/2020
331 |  | 0 |  |  | Request for Information | Rough Openings Doors West End Historical | Rough openings is from face of LVL to face of LVL for width and from finish floor to LVL for height. LVL needs to go the full width of the wall and not between wood trim as shown on architectural details. See attached sketches. The LVL does not need to be 1- 3/4” thick for doors with paneled jambs. This could be some cost savings. Does the rough buck need to be fire rated as this wood is capture behind drywall? |  | I do not have a strong preference to the exact location of the LVL, but still unsure of why it cant be installed as shown in the details. This is really a means and methods item to be coordinated with the millwork sub. please keep the LVL at 1-3/4" as detailed. No the LVL does not need to be fire-rated. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/27/2020 |  |  |  |  | Closed | 04/03/2020 | 04/30/2020 | 04/23/2020 |  | 03/27/2020
332 |  | 0 |  |  | Request for Information | CCD 006r3 |  |  | Please follow the most current CCD. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Westland PE’s |  | 03/27/2020 |  |  |  |  | Closed | 04/03/2020 | 03/30/2020 | 03/30/2020 |  | 03/27/2020
333 |  | 0 |  |  | Request for Information | Soda line conduit | What size conduit is required for the soda lines there are 2 different sizes on the drawings? If they are 6" because of the 24" distance between the mat slab and the rat slab the curved portion of a 90* bend will be above grade. (we can cut this down it will make the conduit end oval shaped and bushings would not be able to be installed) |  | due to some pending design changes.......this question my become irrelevant. soda line likely no longer needed ¦ this information will be provided in a forthcoming ccd ¦ ¦ im going to leave it open until we know for sure it is irrelevant |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/30/2020 |  |  |  |  | Closed | 04/06/2020 | 05/11/2020 | 05/08/2020 | 03/30/2020 | 03/30/2020
334 |  | 0 |  |  | Request for Information | East Rooms Excavations | We have 3' 5" we need 5' from top of slab to top of finished floor this is needed to add the duct work in this area. If this area is to have concrete, we will need the depth of the concrete (4”) and any sub-base depths (6”) Please advise For reference I have attached some information showing what is needed and what we have. Stone at doorways will need to be cut down 5' to allow for ducting as shown on drawings. Please advise |  | No new basement floor slab is required in these east room areas. The soil can be excavated as required for the duct to be installed. ¦ There are no floor slabs to be added in these areas. Excavate soil to accommodate new ductwork. see Response from ARW. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/30/2020 |  |  |  |  | Closed | 04/06/2020 | 04/01/2020 | 03/31/2020 |  | 03/30/2020
335 |  | 0 |  |  | Request for Information | Annex stair 2 shaft dimension clarification | Please clarify the dimension to the CMU stair 2 walls at the annex basement: 1) AE147 between grids A5 to A6 the stair 2 shaft shows a dimension of 9'-3" which appears to be the west face of CMU to the east face of existing wall along grid AH. When we use the east dimension of 14'-8 1/2" and 5'-6 1/2" from grid AG this only leaves around 9' +- 1" between inside face of CMU and existing concrete. Will this work for the clear opening? The step in the existing wall shown on detail C1/AE382 does not exist. The clear dimensions on C1/AE382 add up to 8'-10 1/4" but that also includes the fur out. 2) AE146 calls out a dimension of 9'-10" from existing wall but it also shows a step in the wall but this does not exist as mentioned in question #1. The east/ west dimension of 19'-7" from grid AG to east face of CMU would be the dimension we use if this gives the correct clear dimension inside. |  | CMU Wall that runs N/S should have East Face 19'-7" from Grid AG CMU Wall that runs E/W should have South Face 22'-9" from Grid A6 Slab opening will run from West face of N/S CMU Wall to Existing Foundation Wall Clear opening will run from North face of E/W 12'-8" to the North. Top of foundation/slab elevation still needs to be 100'-0" to receive Precast Panels. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 03/30/2020 |  |  |  |  | Closed | 04/06/2020 | 04/06/2020 | 04/01/2020 | 03/30/2020 | 03/30/2020
336 |  | 0 |  |  | Request for Information | Sealer Gasket @ Acoustically Insulated Walls | Note 12 in spec section 092217-7 calls for the install of "sealer gasket at the underside of wall bottom track at acoustically insulated walls." Our interpretation of "acoustically insulated walls" refers to STC rated walls only. Please advise if acoustically instulated walls only refers to STC rated walls as referenced on the Wall Types sheets in GA drawings (GA002-GA004). |  | Sealer Gaskets are to be installed at bottom tracks of all walls that reference an STC rating or acoustical insulation on Wall types (sheets GA002 - GA004). ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/16/2020 | 04/15/2020 | 04/01/2020 | 03/31/2020
337 |  | 0 | 321313 |  | Request for Information | CONCRETE PAVING | Hand tooling and saw cutting the radius curves in the sidewalks isn't working. Per a conversation with Chris Robbins we are proposing the attached method. Please advise if this is acceptable. | See the attached suggestion. | The proposed method of pouring the bands first and the center second is acceptable, please proceed. ¦ |  |  | High | Camron Walker | Westland Construction, Inc. | Landscape Architects |  | 03/31/2020 |  |  |  |  | Closed | 04/03/2020 | 04/09/2020 | 04/02/2020 | 03/31/2020 | 03/31/2020
338 |  | 0 |  |  | Request for Information | Corridor Columns on 3rd and 5th Floor | Plans show columns at 3rd and 5th floor corridors, but these columns have been demolished. Floor plans show columns to be existing. Please advise if the corridors on the 3rd and 5th floor will be receiving new columns. If so, please provide the design of the new columns; wood/metal stud framed? |  | The new bump-outs at the Hallways are to be wood framed. Match the width of the existing truss and depth of the bump-out on the opposite side so that they are consistent and equal. See the door schedule on sheet AE602 for opening sizes. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 05/14/2020 | 05/12/2020 | 04/01/2020 | 03/31/2020
339 |  | 0 |  |  | Request for Information | Partial/Full Height Walls | There is no schedule providing a break down of which walls are partial height and which are full height. When viewing the building sections, it is unclear whether some walls are partial/full-height. Please advise if the highlighted walls are partial height walls. |  | Please see attached for response. ¦ |  |  | High | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/16/2020 | 04/14/2020 | 04/01/2020 | 03/31/2020
340 |  | 0 |  |  | Request for Information | Waiting 109 & Chapel 110 column dimension conflict | There are conflicting dimensions in the Waiting #109 and Chapel #110. Please advise which dimensions we are to construct with. |  | See ASI-021 showing revised column dimensions. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 05/14/2020 | 05/13/2020 | 04/01/2020 | 03/31/2020
341 |  | 0 |  |  | Request for Information | Cove Detail Material Not Specified | Sheets AE4105-4107 show a material to be installed in multiple rooms at ceiling corners. D5/AE570 does not specify the type of material. Please advise what material is to be installed at the corner in the Cove Detail D5/AE570. |  | The Cove material in these areas are gypsum board. ¦ This cove to be provided as a curved gyp board assembly or as GFRG. We are open to discuss the options and weigh the pro's and con's of each. my opinion is this ought to be constructed from GFRG. ¦ ¦ I just added another attachment because maybe it was unclear. What material is the curved molding? |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 05/11/2020 | 05/08/2020 | 04/01/2020 | 03/31/2020
342 |  | 0 |  |  | Request for Information | Wall Type and Fire Code Discrepancy | Wall type #76 calls for a 2-hr rated wall. One GA201A, #76 wall types are being called out as 1hr rated walls. Please advise if the Fire Code plan supercedes the Wall Type sheet. |  | Please follow the code plans. Fire rated walls are only applicable where indicated on the code review plans. Wall type 76 is to be constructed the same way shown per wall type detail even if it is not considered a 2-hour fire rated wall. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 05/14/2020 | 05/13/2020 | 04/01/2020 | 03/31/2020
343 |  | 0 |  |  | Request for Information | Room #510 ceiling height | On sheet AE125, most rooms show a ceiling height of 9'-3", but room #510 shows a ceiling height of 9'-4". Please advise if this room's ceiling height is to match with adjacent rooms. |  | Yes, Rm 510 should match the adjacent room ceiling heights at 9'-3". ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/10/2020 | 04/09/2020 | 04/01/2020 | 03/31/2020
344 |  | 0 |  |  | Request for Information | Door Openings East of Baptistery | It appears that the doors indicated in yellow on the attached (82” above finished floor) in the north rooms on the Baptistery level will need to have the headers cut out to allow for the new doors. The new doors are going to need to be cut in allowing for 88” above finished floor for R.O. plus 10” for the lintel. The width will also be impacted because we have a 36” door with 8” on each side for the concrete then 4”to allow for the door frame and shimming this is equal to 62” overall. Please advise. |  | Due to the current condition of the opening in the stone wall, we anticipate cutting the existing door height taller, but the width will stay the same and not be cut any wider. Any new opening support will need to fit within the opening without the opening being cut wider. Use detail 8/S240 for reinforcing this new taller opening with the following modifications. The new concrete header thickness spanning the opening needs to be increased to 12" deep instead of 10". The thickness of the new concrete side walls can be reduced from 8" to 6" thick and must be reinforced with #5 vertical bars @4" o.c. instead of 8"o.c. Please verify that a 6" thick new concrete wall thickness will still allow the proper door size to fit without cutting the existing opening wider. ¦ see response from ARW |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/14/2020 | 04/13/2020 |  | 03/31/2020
345 |  | 0 |  |  | Request for Information | Rough Opening for Wood Shimmed Door Jambs | What is our rough opening of metal framing, from metal to metal, for wood jambs/doors when wood shimming Jamb details on AE602-603. |  | A door schedule will be provided by the door manufacturer that will include rough opening sizes. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/30/2020 | 04/30/2020 | 04/02/2020 | 03/31/2020
346 |  | 0 |  |  | Request for Information | Steel Beam Spacing - ANNEX | Reviewed drawings came back with numerous spacing issues. GSW requests a phone review at Engineer's convenience to discuss. |  |  |  |  | Medium | Brett Glassey | Glassey Steel Works | Westland PE’s |  | 03/31/2020 |  |  |  |  | Closed | 04/07/2020 | 04/02/2020 |  |  | 03/31/2020
347 |  | 0 |  |  | Request for Information | Baptistery Cove Lighting | The cove lights in the baptistery are called out as type TLC This is a 4100k wet location tape light that is described as being for the monument sign , the recessed cans in the same location are type DR6M which are 2700k. Fixture type TLB is a 3000k indoor tape light that described as being ceiling cove mounted it has the same lumin output as the TLC and is much closer to the color temp of the DR6M cans . we would suggest changing these tape lights to the type TLB. Please Advise. |  | I reviewed the Lighting Fixture Schedule and I agree that the LED Light Strip in the Baptistry Ceiling Cove should be Fixture Type: TLB DT. ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 04/01/2020 |  |  |  |  | Closed | 04/08/2020 | 04/20/2020 | 04/20/2020 | 04/17/2020 | 04/01/2020
348 |  | 0 |  |  | Request for Information | Mulberry Tree 57 Cabled and Braced | Per the march arborist report mulberry tree #57 Needs to be cabled and braced before the leaves come on. Please advise. |  | Please see attached response. ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 04/01/2020 |  |  |  |  | Closed | 04/04/2020 | 05/20/2020 | 04/03/2020 | 04/02/2020 | 04/01/2020
349 |  | 0 | 085200 | AE640 & AE652 | Request for Information | Window Type Clarifications in the Annex | Re-View RFI 3 Item #1: Window Type B as shown on sheet AE640 has been deleted and replaced with typical Window Type C per our conversations with Scott Gilberg on 03/09/2020. These changes will be reflected in our Annex shop drawing submittals this week. Item #2: The architectural precast rough openings (width only) for Window Types A & D Tri-arch openings have changed. See attached pdf elevation drawing from Scott Gilberg. These changes will be reflected in our Annex shop drawing submittals this week. Item #3: The GFRC brickmold trim as shown on AE652, Window Types A & D Tri-arch has been deleted and replaced with wood brickmold trim. See attached pdf email from Scott Gilberg. These changes will be reflected in our Annex shop drawing submittals this week. |  | The items stated by Review are correct. and will be reviewed in the shop drawings |  |  | High | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/10/2020 | 04/30/2020 | 04/27/2020 |  | 04/01/2020
350 |  | 0 | 085200 | AE640 & AE652 | Request for Information | Historic Windows Type H5, H4 & K Clarifications | Re-View RFI 5 Item #1: Please confirm Window Type H5 (Full Circle Units – Qty: 18 – on the 5th floor) as shown on floor plan sheet AE105 are to be operable, pivot style sashes. Item #2: Please confirm Window Type H4 (Full Circle Units – Qty: 4 – on the 5th floor) as shown on floor plan sheet AE105 are to be fixed, non-operable sashes. Item #3: Please confirm Window Type K (Full Circle Units – Qty: 6 – on the 5th floor) as shown on floor plan sheet AE105 are to be fixed, non-operable sashes. Item #4: Please confirm Window Type H5 & K (Full Circle Units – Qty: 24 – on the 3rd floor) as shown on floor plan sheet AE103 are to be fixed, non-operable sashes. This RFI is driven from conversations between multiple individuals within the design team and facilities department over the last several months. |  | None of the windows will be operable. Therefore the Windows do need to have the same appearance of an operable window such as double hung etc. |  |  | High | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/10/2020 | 04/07/2020 | 04/02/2020 |  | 04/01/2020
351 |  | 0 | 085200 | AE640 & AE652 | Request for Information | Historic Windows Type H2 - 4th Floor | Re-View RFI 6 Item #1: Previously, on September 23rd, 2019 pricing was submitted to change the lower window sash from “Fixed” to operable on Qty: (16) Type H2 window openings on the 4th floor. This would apply to the window openings in the Assembly Room only. See attached |  | After discussions with the client, as of March 2020 there will be no operable windows. |  |  | High | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  | 16281.00 | Closed | 04/10/2020 | 04/22/2020 | 04/17/2020 |  | 04/01/2020
352 |  | 0 | 235216 |  | Request for Information | Boiler voltage | Reference attached page from boiler (B1, B2, B3) submittals. This lists both 208V and 480V electrical requirement. The electrical plans call for (1) 480V 3Ø circuit to these boilers. What is the voltage? Is a starter required? typically boilers do not need starters. |  | Keep 480V as designed, unless manufacturer recommends otherwise, then notify engineer in writing for design change. If manufacturer does not require starter, then only provide disconnect as required by NEC. RFI to be reviewed and responded to by VBFA as well. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 04/01/2020 |  |  |  |  | Closed | 04/08/2020 | 04/10/2020 | 04/09/2020 | 04/02/2020 | 04/01/2020
353 |  | 0 | 230000 | M103, S103 | Request for Information | Level 4 duct penetration at floor | Drawing M103, gridline HF is shown two 60"x24" ducts that rise up to level 4. Drawing S103 at this same location is showing new ceiling joists with no openings for the ducts. See attached clouded drawings for clarification. | Please provide structural openings of to allow for two 62"x26" lined ducts at level 4. | Openings in ceiling framing will be shown in a forthcoming CCD. ¦ See answer from ARW (Structural) ¦ This response will be part of the upcoming CCD-37 R.2. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/08/2020 | 05/05/2020 | 05/05/2020 | 04/02/2020 | 04/01/2020
354 |  | 0 | 220000 | P099, CCD#035, 035r1 | Request for Information | CCD#035 r1 floor drains | Drawing P099, CCD# 035 r1 does not appear to indicate any size for the underground sewer waste serving the new floor drains at shop area 041. Also, floor drain sizing as shown in CCD#035 was discussed with VBFA/Westland to be changed in r1 documents to include six 2" FD's and one 4" . This change does not appear to have been made. See attached for clarifications. | Please provide underground waste piping size and confirm if floor drain sizing is to be changed per previous VBFA/Westland conference call. | see response from VBFA. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/08/2020 | 05/05/2020 | 05/05/2020 | 04/06/2020 | 04/01/2020
355 |  | 0 | 233423 | EP601 and 233423 Submittals | Request for Information | Exhaust Fan Voltage Discrepancies | Reference attached list of exhaust fan voltage discrepancies and advise. (EF-0.01, EF-1.04, EF-1.05, EF-1.06, & EF-1.07) |  | Envision was not provided Exhaust fan submittals for review or notified of design change of voltages previously. Provide fans with electrical specifications as designed. If it is not possible for the fans to be supplied with voltages, phase as designed; the complete updated data for each fan including, voltage, phase and HP or amps will need to be provided to Envision engineering, so that design revisions can be prepared to update conduit, wire, breaker sizes and disconnects/starters as necessary. CCD# will need to be provided to Envision for tracking of changes. RFI to be reviewed and responded to by VBFA as well. ¦ ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/01/2020 |  |  |  |  | Closed | 04/08/2020 | 04/14/2020 | 04/09/2020 | 04/10/2020 | 04/01/2020
356 |  | 0 | 114000 | EP601 Kitchen Eq. Schedule | Request for Information | Kitchen Equipment Voltage | Reference attached submittal for kitchen item #1.075 dishwasher, 208V 3-phase. It is 480V on the electrical plans. Please advise. Also, confirm this is a two-point connection with separate booster heat circuit per electrical plans. Confirm voltage of items #1.65 & #1.77 disposals. They are 480V on the electrical plans. |  | these items to be resolved in a forthcoming ccd. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/02/2020 |  |  |  |  | Closed | 04/09/2020 | 05/11/2020 | 05/08/2020 | 04/02/2020 | 04/02/2020
357 |  | 0 |  | M103, AE123, AE183 | Request for Information | Initiatory Sink Rough In | Due to the coordination needed to be done between the HVAC and the Plumbing. Please provide the location and rough in requirements for the initiatory sinks on level 3. |  | The locations and types of fixtures for the initiatory fixtures is under review with project ownership. however a 'bootlegged' version of the fixture and its location has been provided to the contractor. ¦ |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/02/2020 |  |  |  |  | Closed | 04/03/2020 | 04/23/2020 | 04/09/2020 | 04/02/2020 | 04/02/2020
358 |  | 0 |  |  | Request for Information | Historical Roof Demo | Please confirm the roofing is to be demoed by the roofing contractor and not by the abatement contractor. Costs will be associated with this change. |  | Please refer to CCD-11 R.9 for response. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/02/2020 |  |  |  |  | Closed | 04/09/2020 | 04/16/2020 | 04/15/2020 |  | 04/02/2020
359 |  | 0 | 328400 | Detial 1/LI503, Irrigation Schedule LI100 | Request for Information | Irrigation Backflow Preventer | The specified reduced pressure backflow preventer for this project is a 2" Zurn Wilkins 375XL. We have been informed that the Temple recently purchased a 3" Zurn Wilkins 375AST reduced pressure backflow preventer which is new and still in the crate (see attached photo). We have ordered the 2" 375XL specified, but it has not been delivered, and I have placed a hold on it pending a response to this RFI. Instead of furnishing and installing the 2" 375XL, would you like us to use the 3" 375AST that the owner already has? The following is information for your comparison: 2" 375XL has an optimal flow rate of ~170 GPM with 13 psi pressure loss (see attached data sheet), and it has an overall length of 24" when installed. 3" 375AST has an optimal flow rate of 500 GPM with 11 psi pressure loss (see attached data sheet), and it has an overall length of 57" when installed. The mainline on this project is a 4" complete loop, and there are 86 irrigation zones flowing through this point of connection. If we use the 3" 375AST, the backflow enclosure size would have to be changed to accommodate the larger backflow which would be an additional cost that would exceed the credit we could provide by not furnishing the 2" 375XL. It is my feeling that the irrigation designer has provided you with the best cost/value design using the 2" 375XL for this system. Changing to the 3" 375AST would increase the capacity of the point of connection substantially and allow for a shorter watering window, but would come at an additional cost for the larger enclosure and piping. Please advise. |  | MGB+A Response: We prefer to stick with the original design approach from the contract documents. However, the provided alternative option of switching to the 375AST does have some merit. Please provide complete cost break down that shows the cost for alternate backflow enclosure and possible credit. We will need the cost comparison information before we can provide further recommendations. MGB+A: Brandon Ruiz 4-3-2020 ¦ MGB+A Response: Thank you for providing pricing for the RFI 359. We will not be selecting this option at this time. Please continue with the backflow and related equipment and installation as provided in the plan drawings. MGB+A: Brandon Ruiz 5-8-2020 ¦ ¦ |  |  | Medium | Tim Maynes | Stratton & Bratt Landscaping | Landscape Architects |  | 05/08/2020 |  |  | 3000.00 |  | Closed | 04/09/2020 | 05/08/2020 | 05/08/2020 | 04/07/2020 | 04/02/2020
360 |  | 0 |  |  | Request for Information | Stair 3 CB5 beam at 12" suspended slab | Reference S100B, AE386 There is a CB5 beam shown north of grid H3 between HH and HG at the 12" suspended slab at level 0.5. This beam does not show up in the BIM model and is not shown on architectural sheets on AE386. This beam is typical at the upper floors for the stair stringers connect per details 4,12/S212. Please verify if this beam is needed below the level 0.5 suspended slab. *After reviewing with mechanical subcontractor it conflicts with mechanical duct that runs below it. |  | This beam is required per the drawings. Please coordinate and route mechanical elements below this beam. ¦ ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 04/03/2020 |  |  |  |  | Closed | 04/09/2020 | 05/20/2020 | 05/18/2020 | 05/15/2020 | 04/03/2020
361 |  | 0 |  |  | Request for Information | Floor Box Locations | Please provide dimensioned layout for all electrical floor boxes. |  | Please see the attached floor plan layouts for each floor showing the dimension locations of the floor boxes. There will also be an upcoming CCD regarding the floor boxes in the West tower Addition. These have been removed and will be wall mounted outlets in the new furring at the historic stone wall. Please coordinated accordingly. |  |  | High | Westland PE’s |  | CRSA ARCHITECTURE |  | 04/28/2020 |  |  |  |  | Closed | 04/06/2020 | 04/30/2020 | 04/28/2020 |  | 04/03/2020
362 |  | 0 | 220000 | CCD#029 P-100 | Request for Information | CCD#029-Added backflow preventer | Per CCD#029 narrative, reference drawing P100, line item #3 indicates to add a backflow preventer. Drawing P-100 within the CCD does not include a new keynote or show location of the new backflow preventer. No type/model/size is offered. | Please clarify if a new back flow preventer is desired. If so, provide location, size, model, etc. | See response from VBFA. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/03/2020 |  |  |  |  | Closed | 04/10/2020 | 05/11/2020 | 05/08/2020 | 04/06/2020 | 04/03/2020
363 |  | 0 | 220000 | P sheets | Request for Information | CCD#029 R.1-Domestic Water Plumbing intent | CCD#029 R.1, narrative, general note for all domestic plumbing sheets reads as follows: 1-Provide price estimate for all domestic plumbing to be aquatherm 2-Provide price estimate for all domestic plumbing to be Nupi Niron 3-Provide price estimate for all domestic plumbing to be PEX Please confirm that pricing is desired for ALL scopes of domestic water piping throughout both the Historic and Annex buildings. | Confirm intent of request for estimate is for all domestic water piping throughout the Historic and Annex buildings. Provide additional direction on PEX piping(IE: Type of PEX pipe, joint type, PEX piping to what max size, 2"?) | please see response from MEch engineer ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/03/2020 |  |  |  |  | Closed | 04/10/2020 | 04/27/2020 | 04/27/2020 | 04/06/2020 | 04/03/2020
364 |  | 0 | 220000 | CCD#032-P601 | Request for Information | CCD#032-Soap Dispenser located in wall cavity | CCD#032, soap dispenser revision, drawing P601, fixture schedule, fixture L-1 description states "Provide MAC Faucets PYOS-109 electronic, sensor, bulk soap dispenser with chrome finish, hard wired AC power connection, with soap container in wall cavity below lavatory". No wall cavity/access detail was provided. The dimensions of the soap dispenser pump/soap bottle are attached. What are the dimensions of the proposed wall cavity to be? Note that plumbing piping in wall will include 2" p-trap waste and 1/2" hot and cold piping. Also shown are hose bibs to be located at these single use L-1 and L-3 lavs. | Please provide proposed wall cavity dimensions and locations to be installed beneath L-1 and L-3 lavatories. We have concerns locating the soap dispensers and hose bibs behind cavity access doors/panels due to access door operation, coordination with plumbing piping and potential water damage from hose bib malfunction. More coordination between owner/design/GC/plumbing is needed to proceed with pricing. | access panels to conceal hose bibs, clean outs and soap containers is no longer a design option. Please refer to ASI #17 where plumbing items are to be wall/surface mounted under lav's in a manner that hides them as much as possible. Arch and plumber to consult on site about preferable and general locations of these items. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/03/2020 |  |  |  |  | Closed | 04/10/2020 | 04/15/2020 | 04/14/2020 | 04/06/2020 | 04/03/2020
365 |  | 0 |  |  | Request for Information | Column Wrap Connection (L2 - L3) | Please see attached sketches of possible bolted connections for the 1/2" Plate Wraps at the (14) columns between level 2 and mezz level. Please advise if this is an acceptable connection - as welding in place cannot happen. |  | ¦ ¦ In order to do a bolted connection it appears that the decorative column quatrafoil wraps will not fit. We have been told that this is not acceptable. Please continue with the initial directive of installing two full height peices of steel that will clam-shell together and be wrapped with FRP. The horizontal joints in the steel can be welded together out of the way of the historic structure and then brought into the bulding as a full height piece. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/04/2020 |  |  |  |  | Closed | 04/11/2020 | 04/09/2020 |  | 04/09/2020 | 04/04/2020
366 |  | 0 |  |  | Request for Information | Two way Communication | the engineers review is asking us to coordinate control panel and call station locations with owner/architect and whether or not control panel should be flush mount. See attached Engineer review. |  | this has been reviewed by A/E team. this is now an item for owner and elec sub to coordinate. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/06/2020 |  |  |  |  | Closed | 04/13/2020 | 04/23/2020 | 04/23/2020 | 04/16/2020 | 04/06/2020
367 |  | 0 |  |  | Request for Information | Inititory Lighting | The lighting in the 3rd floor initiatory rooms shows the circuit going thru a relay and then an occupancy sensor. is the occupancy sensor necessary or should we just put a manual switch in each room to operate them independently as long as the relay is closed similar to sealing rooms on 5th floor. Please Advise |  | Those rooms will have local toggle switch and be routed through relay per plans. Details will be updated in CCD-044 ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 04/06/2020 |  |  |  |  | Closed | 04/13/2020 | 05/07/2020 | 05/06/2020 | 04/29/2020 | 04/06/2020
368 |  | 0 | 144216 |  | Request for Information | Vertical Wheelchair lift | The submittal for the wheelchair lift it calling for a dedicated analog phone line. The electrical drawing don't show this please advise if this analog phone line is needed or not. |  | Provide phone line as required by manufacturer. ¦ See response from Envision. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/06/2020 |  |  |  |  | Closed | 04/13/2020 | 04/30/2020 | 04/30/2020 | 04/06/2020 | 04/06/2020
370 |  | 0 |  |  | Request for Information | Chimney Infills | Do the existing chimney flues in the exterior walls of the historical building going from level 0.5 to the roof need to be infilled with concrete? |  | please see response from ARW ¦ ¦ We recommend that all of the chimney flues be grouted solid. Please limit grout heights to 10' at a time when grouting to reduce chances of blowing out stone or leakage through the stone. |  |  | Medium | Westland PE’s |  | CRSA ARCHITECTURE |  | 04/06/2020 |  |  |  |  | Closed | 04/13/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020 | 04/06/2020
371 |  | 0 |  |  | Request for Information | Core Holes Aligning with Steel Saddle | Upon installing the steel saddle on the stone column at grid line H2 and HB.5 it was discovered that the holes that have been cored through the stone column did not line up with the bolt holes in the saddle. Please confirm that it is acceptable to elongate the hole to receive the Bolt and install a plate washer that will cover the hole and be welded to the steel saddle. |  | ¦ It is acceptable to elongate the holes and provide plate washers that are welded to the steel saddle. |  |  | High | David Adams | Westland Construction, Inc. | Brett Glassey | Glassey Steel Works | 04/06/2020 |  |  |  |  | Closed | 04/09/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020 | 04/06/2020
372 |  | 0 |  |  | Request for Information | Level 2 Floor Structural Upgrade | Please confirm the following direction given on site regarding the steel column saddle installed on the Level 2 floor. The oversized Core holes going through the stone columns are to be grout filled. The plate washers covering the oversized holes in the steel saddles are to have plate washers installed covering the holes and then wielded in place to the steel saddle. The holes for the epoxy bolts on the on the beam side of the steel saddle are to be moved approximately 2” closer to the center of the returning leg of the saddle. |  | 1- Oversized core holes are to be filled with epoxy. 2- Plate washers must be welded to the steel saddle with 1/4" fillet welds all around washer. 3- Confirmed ¦ SEE RESPONSE FROM ARW |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/07/2020 |  |  |  |  | Closed | 04/10/2020 | 04/10/2020 | 04/09/2020 |  | 04/07/2020
373 |  | 0 |  |  | Request for Information | East Side Area Well of Historical | Please advise if this area well with the grate needs to be chipped down below the grade, completely removed or filled back with concrete. The inside of the area well is going to be filled with concrete. |  | Since the area well is not being used by VBFA it will need to be removed and filled-in with soil to be part of the landscape area. ¦ ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/07/2020 |  |  |  |  | Closed | 04/14/2020 | 05/05/2020 | 05/04/2020 | 04/30/2020 | 04/07/2020
374 |  | 0 |  |  | Request for Information | Shear wall coordination meeting at west historic | Reference sheets S250, S251, S252, S253, S254, S255, S222 and attached rebar detail. Per onsite meeting with Innovative, rebar detailer, Westland and ARW please confirm the following: 1) As detailed at the corners on the attached shop drawing it is ok to use 180 degree hooks on the horizontals rebar to tie in the corners at the jamb columns? 2) Confirm acceptable to stagger splice horizontal wall rebar? 3) At area well walls it is ok to use formsavers on the horizontal bar? 4) Per details 2,4,7/S222 confirm it is acceptable have the #4 hook dowels for the suspended slab turn vertical into the suspended slab or wall pour versus cast in the wall below? |  | 1) Yes, 180 degree hooks are acceptable 2) Yes, stagger the horizontal wall rebar splices 3) Yes, form savers are acceptable at area well horizontal bar tie in to perpendicular walls 4) Yes this is acceptable to have hooked dowels turned vertical. ¦ please see response from ARW ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 04/07/2020 |  |  |  |  | Closed | 04/14/2020 | 04/09/2020 | 04/09/2020 | 04/08/2020 | 04/07/2020
375 |  | 0 | 233113 | M100A | Request for Information | Baptismal Font Exhaust Duct Material | Drawing M100A, duct serving Exhaust Fan EF-0-01 does not appear to have any notes or direction as to what type of material to build this ductwork from. Specification section 233113 does not appear to include this type of duct/system within its information. See attached drawings for clarification. Please provide a narrative/specification of what type of duct metal material is to be used or the font exhaust system, whether is requires liner or wrap, etc. |  | For the baptistry exhaust ductwork (fan system EF-0-01). provide the following: • Provide standard galvanized ductwork per specification 23 3113, section 3.12.A and section 3.12.G, item 1. • Provide duct liner per specification 23 3113, section 3.12.K, item 3. ¦ See response from VBFA. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/07/2020 |  |  |  |  | Closed | 04/14/2020 | 05/05/2020 | 05/04/2020 | 04/08/2020 | 04/07/2020
376 |  | 0 |  |  | Request for Information | Room 219 Ceiling Height | Please advise if the ceiling in room 219 is to be installed at 8’-7/8” as called out on sheet AE122 or if it is to be moved up closer to the 13-foot mark as scaled on sheet AE4211. For reference I have included a picture of the room showing where the 8-foot mark will end up on. |  | The ceiling in this location will indeed be roughly 13' above the floor level in this room. The ceiling will be attached to the underside of the floor structure above. the ceiling elevation tag indicating 8' is incorrect. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Aaron Bowers | Pete King Commercial | 04/08/2020 |  |  |  |  | Closed | 04/15/2020 | 04/14/2020 | 04/13/2020 | 04/14/2020 | 04/08/2020
377 |  | 0 |  |  | Request for Information | LFTA Strap Discontinued | Detail 1/S260 calls for LFTA Strap at each stacked stud. This particular strap has been discontinued. Can you get me an alternate? I propose CS16 Coil strapping. |  | We take no exception to using a CS16 strap in lieu of the LFTA strap. Please connect the strap with SD9 screws and predrill holes prior to installing screws. ¦ please see response from ARW ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/09/2020 |  |  |  |  | Closed | 04/15/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020
378 |  | 0 |  |  | Request for Information | Level 3-5 Elevator Fill In | On Levels 3,4 & 5. It calls for (2) 2X12s or 2 1 3/4" X 9" LVLs. Existing floor joists are 2X12s and I propose 1 11 7/8" @ 12 O.C. To match existing floors. I can Notch and place back in original 2X12 pockets and add facemount hangers. Then I will need the allowable floor load for face mount hanger depending on what floor joist we use. |  | Structurally we take no issue with this substitution provided there is no interferance with anticipated mechanical and electrical systems due to the 12"o.c. layout. The facemount hangers need to have a minimum capacity of 1,000lbs. Please allow CRSA to respond to this as well. ¦ ¦ Please review and respond as needed. |  |  | High | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 04/09/2020 |  |  |  |  | Closed | 04/12/2020 | 04/10/2020 | 04/09/2020 | 04/09/2020 | 04/09/2020
379 |  | 0 |  |  | Request for Information | Ledger Board Attachment to Hist. Truss | This is in response to the Question about the 1 3/4" X 9 1/2" LVL Ledger board we propose to install on existing beam with the dowells protruding out. There was a question about Notching out holes to save dowells for historic. My concern is that if we notch out for the dowell and the hole is inline with where the new hanger will attach to the Hanger will not be installed with the required nailing or screws to withstand the floor load required. |  | See comment from ARW. ¦ See comment ¦ We originally requested these to be 9 ½” to allow for tile, grout beds and sloping to the drain. Can we use the 9 ½” 12” O.C. ¦ see ARW's response. ¦ A facemount hanger HU9 is appropriate. ¦ Due to the concern with wood dowel interference. Please use 1-3/4" x 11-7/8" LVL joist spaced at 12"o.c. at the infill areas for the bathrooms instead of the currently specified 9-1/2" LVL's. Install the new LVL joist into the existing joist pockets and then install a top flange hanger similar to what is shown in detail 5/S246. This change will be made in a forthcoming clarification. ¦ Correction. In the bathroom areas a 1-3/4" x 9-1/2" LVL @ 12"o.c. can be for the joist. ¦ A top Flange hanger is designed for a joist being attached to a equal size member. We are attaching a 9 1/2" LVL to a 12" rough sawn member. Would like to substitute top flange hanger with facemount hanger HU9 that has an allowable floor load of 2680lbs. |  |  | Medium | David Rockhill | Rockhill Construction | Structural Engineers |  | 04/16/2020 |  |  |  |  | Closed | 04/16/2020 | 04/22/2020 | 04/16/2020 | 04/15/2020 | 04/09/2020
380 |  | 0 |  |  | Request for Information | Replace Roof Purlin | S106 Line HF- H5 it instructs to replace roof purlin that is broken with a 3 1/2" X 7" PSL. I know we are tight on room bc of HVAC and location makes it a difficult fix. Then beam goes all the way back to at least line HE. Which makes it over 24' long. I was informed there will be a hole cut for HVAC to go thru to stairway. May I propose Cutting existing beam in center of 2 roof trusses between Lines HF and HE. FYI the other beams above and below this one are cut on the center of those trusses. Then I would propose to install (4) 1 3/4" X 11 7/8" LVLs To replace beam as a substitute for PSL. Strap the new LVLs to the end of the Beam where the splice occurs with Manufactured metal strap with thru bolts. Please see attached pictures. Let me know solution so I can get an estimate to reflect what we are to do. |  | please see response from ARW ¦ After discussion with the contractor it was learned that the existing purlins are deeper than 7". It is acceptable to use (4) 1-3/4" LVL's that are cut to match the depth of the existing purlins. ¦ ¦ It is acceptable to cut the purlin over the truss and join the new purlin with the old purlin using a Simpson PS418 strap. In order to maintain adequate room in the attic space, please continue to use the PSL beam specified. |  |  | Medium | David Rockhill | Rockhill Construction | Structural Engineers |  | 04/14/2020 |  |  |  |  | Closed | 04/16/2020 | 04/15/2020 | 04/14/2020 | 04/10/2020 | 04/09/2020
381 |  | 0 |  |  | Request for Information | 5th floor outlets for lamps | 5th floor corridor 516 and 520 both have several electrical outlets for lamps that are dimensioned on the interior elevation drawings at the same elevation as a horizontal beam please advise (see attachments) |  | Due to the wood beam being in the way, the elec outlets may be installed below the beam. It appears that the boxes could be installed at 17" above the floor, to center of the outlet. Please ensure that the boxes are consistent in installation height. ¦ ¦ Structurally, the horizontal beam needs to stay in place and should not be cut for the outlet boxes. We suggest moving the boxes up or down to miss the beam. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/10/2020 |  |  |  |  | Closed | 04/17/2020 | 04/14/2020 | 04/10/2020 | 04/10/2020 | 04/10/2020
382 |  | 0 |  |  | Request for Information | Shear Wall Connection to Steel Columns | Is it possible to replace the detail noted on the GSN (J.8) which requires the steel column to be connected to the concrete wall with 1/2" dba's 24" long with an embed using the same dba's & spacing? Please see attached sketches showing original intent as well as proposed solution. Along with this embed, GSW suggests a 2-3" gap between the wall and column to allow for independent installation. In order to connect the column to the wall GSW suggests using weld plates from the embed to the column after the wall is poured. Please advise |  | Please see response from ARW ¦ The columns must connect to the concrete shearwalls as detailed as they were designed to act as boundary steel and as a drag connecting element. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/10/2020 |  |  |  |  | Closed | 04/17/2020 | 04/15/2020 | 04/10/2020 | 04/10/2020 | 04/10/2020
383 |  | 0 |  |  | Request for Information | Temple Fountains (North & East Fountains) | Please confirm all dimensions boxed in red on sheet 2 of the two preliminary drawings attached here. Once these basic dimensions are confirmed we can begin working on the detailed fabrication drawings. Thank you |  | The general size and form of the fountain is acceptable and in line with the intent of the drawings. See attached for comments regarding the beehive pinnacle and mulberry leaf detail. ¦ ¦ |  |  | Medium | Mark Gabriele | Artisan Granite, LLC | Landscape Architects |  | 04/10/2020 |  |  |  |  | Closed | 04/17/2020 | 05/07/2020 | 05/06/2020 | 05/06/2020 | 04/10/2020
384 |  | 0 |  |  | Request for Information | Sheer Wall Structural Coordination | The first shear wall we have started on at grid AE in the annex has a clash between the mechanical block out shop drawings and embed layout shop drawings. The mechanical blockout is continuous as shown on A/S301. We are working on a coordinated layout and need to know how close to the embed, both vertically and horizontally, can we locate these duct penetration block-outs? (see the attached) | These sorts of penetration coordination issues may be typical in the sheer walls. We hope that you might be able to give us some general direction rather than an approval for each deviation from a sheer wall penetration location. | See response from ARW. ¦ IN this particular instance............the duct (or the block out) can not be moved at all. this duct goes up into the marriage waiting chapel above where the duct grille has been carefully located to center it directly between columns in the room and centered under the circular window above. structural is working up options to relocate that beam and embed. again the duct block out can not move. ¦ See CCD-45R.1 for response. ¦ In general, the blockouts need to be no closer than 12" horizontally to any beam embed plate. As for how close a duct block out can be to an embed plate in the vertical direction; there are too many variables for this to provide a general number. This vertical dimension depends too much on the size of the opening, the amount of load being supported by the embed plate, thickness of the wall, etc. The vertical dimension will need to be reviewed on a case by case basis. ¦ Can you provide a vertical dimension for the duct at the specific location given in the attached drawing? ¦ Please provide detail mentioned by Scott Gilberg. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/13/2020 |  |  |  |  | Closed | 04/17/2020 | 05/14/2020 | 05/06/2020 | 04/14/2020 | 04/13/2020
385 |  | 0 | 283111 | EY Conformed Drawings, FA Shop Drawings | Request for Information | Fire Alarm Device Discrepancies | Part 1. See attached list of fire alarm discrepancies between the conformed EY drawings and the FA shop drawings. Many devices were revised without an addendum or CCD. Please respond to each line item. Part 2. See attached Q&A between Wilkinson Electric and AAA Fire on additional discrepancies or questions. Please respond to each line item. |  | It appears that most of these devices were changes that should have been issued as part of Addendum #6 per clouding on sheets. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 04/13/2020 |  |  |  |  | Closed | 04/20/2020 | 04/23/2020 | 04/22/2020 | 04/15/2020 | 04/13/2020
386 |  | 0 |  |  | Request for Information | 5th Floor Stair Tower Notch | Please confirm that we can enlarge the notch in the top stair towers to 24” from the 18” specified in the drawings. This additional room is needed to allow for more space in the notch to make room for lighting arrestor some condensate line and a 1” conduit electrical line. |  | Making the width from 18" to 24" is acceptable. The new in-fill wall framing and plaster system shall match the existing historic curved wall plane. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/14/2020 |  |  |  |  | Closed | 04/14/2020 | 05/05/2020 | 05/04/2020 |  | 04/14/2020
387 |  | 0 |  |  | Request for Information | Restroom Mirrors at Wall Tile Transition | Please advise as to how the mirror is to be mounted on a tile to Drywall transition. Do we bring the mirror out to the tile level or take it back to the Drywall location and install tile transition peace’s where the tiles terminate into the Mirror? |  | Tile cap will but into mirror. Mirror will go over general wall tile and mount to wall. Add a mounting system to back to allow for gap. See attached drawing. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Interior Designer |  | 04/14/2020 |  |  |  |  | Closed | 04/21/2020 | 08/31/2020 | 08/28/2020 | 05/15/2020 | 04/14/2020
388 |  | 0 |  |  | Request for Information | Annex mat footing waterstop 13/S210 | Reference S100, detail 13/S210 and attached spec for Sika Hydrotite We are having issues getting the specified self expanding 3/4"x 1" butyl strip waterstop (section 031000-2.2) to adhere to the vertical face of the existing mat footing. We have followed the manufacturers recommendations and fastened at 12" spacing and the product is drooping/sagging in the middle. The approved product that we submitted is SIKA swellstop. Per discussions with Westland we were informed that the bottom row of waterstop is being replaced with an injectable product. The top row is still required. We have consulted with our supplier and the attached product called SIKA Hydrotite was recommended. This product has better adhesion qualities and will not sag and droop like the Swellstop product. Please confirm this will work at the annex mat footing. |  | We take no issue structurally with the use of this product provided that the architect and waterproofing consultant is okay with it. ¦ The waterproofing methods described/suggested were approved and used prior to the mat footing being poured. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 04/14/2020 |  |  |  |  | Closed | 04/21/2020 | 05/15/2020 | 05/15/2020 | 04/15/2020 | 04/14/2020
389 |  | 0 | 260573 |  | Request for Information | Revise Gear per Coordination Study | See attached pages from coordination study review. Square D has notified us there will be a cost increase to change to larger frame breakers with LI trip units for those breakers listed in the recommendation table and to upgrade panel HE to an I-Line. These recommendations need to be followed in order to achieve the the required coordination. Is this how we should proceed? Please advise. |  | Provide changes to meet the coordination study as required in the specifications. Provide detailed break out of increased costs for approval. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 04/14/2020 |  |  |  |  | Closed | 04/21/2020 | 04/23/2020 | 04/22/2020 | 04/15/2020 | 04/14/2020
390 |  | 0 | 273244 |  | Request for Information | Two-Way Communication System Monitoring Information | We need to get the monitoring (phone #) information from the Church for the two-way communication system before this order can be put into production. This panel has to be programmed at the factory. See attached programming guide, page 7. |  | this is still an item for the sub-contractor and contractor to gather from the TFM. need to set up a meeting? ¦ We would like that phone number to be "155". Thanks. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Brian Chandler | CORPORATION OF THE PRESIDING BISHOP OF THE CHURCH OF JESUS C | 04/14/2020 |  |  |  |  | Closed | 04/21/2020 | 05/11/2020 | 05/11/2020 | 05/11/2020 | 04/14/2020
391 |  | 0 |  |  | Request for Information | Top of Column Joist Connection - Annex | Please refer to the attached screenshot for the top of column connections for joists . Is it possible to use a bolted cap plate as shown? It appears this will still allow for the drag plates to be installed as designed. |  | see response from ARW ¦ ¦ Yes, assuming this is a picture of the bump up middle high roof area. Detail 1/S230 should be used at the joist to column connections. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/14/2020 |  |  |  |  | Closed | 04/21/2020 | 04/15/2020 | 04/15/2020 | 04/15/2020 | 04/14/2020
392 |  | 0 |  | P602, CCD-029 | Request for Information | Added RCP-2 in CCD-029 | CCD-029, sheet P602 added a new 120V recirculation pump RCP-2 but nothing from the electrical engineer is included. What panel and circuit # are we to use? And will it have a manual starter? |  | Mechanical will coordinate with electrical and a CCD will be issued. ¦ RCP-2 is a new pump to replace the existing pump. We have been told that the pump will be the same voltage and load as the existing pump. We suggest re-using the existing circuit and wire feeding the existing pump and matching or re-using controls that are in place on the existing pump if they are in good condition. If in poor condition replace with new to match existing. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 05/20/2020 |  |  |  |  | Closed | 04/22/2020 | 05/21/2020 | 05/20/2020 | 04/29/2020 | 04/15/2020
393 |  | 0 |  |  | Request for Information | 4th Floor Lattice Truss I-beam Install | In doing the layout for the I-beams that are going to be installed in the floor of the 4th floor. It was discovered that due to the cup in the floor the top flange of the I beam will be intersecting with the bolt on the lattice truss. Please advise. I have attached some photos for reference. |  | please see response from ARW ¦ Please provide a new thru-bolt of same diameter as existing bolt below the existing bolt. Once the new bolt is installed, remove the old bolt. DO NOT oversize the new hole for the new bolt. The new bolt must fit tight within the new hole. Locate the new bolt so the new wide flange beam can be installed without interfering. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/15/2020 |  |  |  |  | Closed | 04/22/2020 | 04/23/2020 | 04/23/2020 | 04/15/2020 | 04/15/2020
394 |  | 0 | 230000 | M101, CCD#028R1 | Request for Information | CCD#028 R1-Missing CFM values | Drawing M101, room 155 and 159 appear to be missing CFM values at the new grill locations. | Please provide CFM values at new grilles. See attached clouded drawing for clarification. | See added CFM values from VBFA. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/15/2020 |  |  |  |  | Closed | 04/22/2020 | 05/07/2020 | 05/07/2020 | 04/30/2020 | 04/15/2020
395 |  | 0 |  | Detail 10, ES501 | Request for Information | Concrete Light Pole Base | Is Detail 10 on sheet ES501 correct? It shows 6'-6" of concrete base buried. The tallest pole we have is 12' and typically these details call for 4'-6" buried depth for a 15' pole and a 6'-6" buried depth would be good for a 30'-35' pole. Please confirm. |  | please see response from ARW ¦ ¦ These poles differ from the poles that the original foundation calculations were done. With the maximum pole height of 12'-0" as shown in the cut sheets, it will be acceptable to use a 4'-6" deep foundation. The foundation diameter and reinforcing will be the same as specified in the current drawings. |  |  | High | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/15/2020 |  |  |  |  | Closed | 04/19/2020 | 04/23/2020 | 04/23/2020 | 04/17/2020 | 04/15/2020
396 |  | 0 |  |  | Request for Information | Room 219 wall framing | Reference AD102 and AE142. Please advise what wall type is to be installed in Room 219. I have attached some drawings for reference. | Suggestion: If the walls ends up being framed rather than plaster on stone, the floor boxes, wall sconces, and light switches would be able to be roughed in the wall framing rather than the stone walls. | indeed providing a furred wall would allow the electrical items to be placed in the wall rather than the floor. However, the remaining and historic door casings in the room do not allow for this room to be furred out. meeting with plaster sub next week to visit the idea that the walls will need to be replaced as plaster on stone once again. so for now we keep the floor boxes ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/15/2020 |  |  |  |  | Closed | 04/22/2020 | 04/23/2020 | 04/23/2020 | 04/16/2020 | 04/15/2020
397 |  | 0 |  |  | Request for Information | Micropiles on Historical South Wall | Do the duct penetrations on the South exterior wall as shown on sheet S100A need to have Micropiles and Needlebeams as shown in sheet S240 detail 9? Please advise. |  | no. openings are small enough and high enough that micropiles not needed. see response from ARW ¦ No. Micropiles are not needed at those penetrations. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/16/2020 |  |  |  |  | Closed | 04/22/2020 | 04/17/2020 | 04/16/2020 | 04/16/2020 | 04/16/2020
398 |  | 0 | 220000 | CCD#29R1-P100 | Request for Information | CCD#29R1-Step Saver Piping-Water Softener System | CCD#29R1, drawing P100 keynote 44 states step saver pipe connects to brine tank. A 6" line, pink in color is indicated routed to cooling tower yard below finish grade at street level. No mention of this piping or system is included in the narrative or shown on equipment schedule drawing P601. | Please clarify if step savor piping and salt delivery system for brine tanks is desired. If so, provide details, etc as needed to allow for pricing to be compiled. | please see response from VBFA-spencer ¦ Please see the attached pdf "RFI_398_CCD_29R1-Step Saver Piping-Water Softener System_VBFA" for the updated RFI response. Brian Oswald, VBFA 30-Apr-2020 ¦ See Response from VBFA. ¦ ¦ ¦ Please provide further information regarding the Step Saver salt delivery system to include model, specifications, etc. to allow correct estimation of costs and installation requirements. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/16/2020 |  |  |  |  | Closed | 04/23/2020 | 05/11/2020 | 05/08/2020 | 04/22/2020 | 04/16/2020
399 |  | 0 | 220000 | P113, P115 | Request for Information | Plumbing Fixture U-1 support carrier requirements | Plumbing fixture urinal U-1 specifications requires that floor mount carriers be used to support the fixture at the wall. At Historic Structure, existing wood subfloor and wall framing make installation of floor mount carriers difficult to secure rigidly. See attached drawings indicating locations where this type of installation is shown. Urinal carrier cut sheet is also attached for reference. Is additional structural modifications necessary at these locations to allow for a correct carrier installation? | Suggest allowing in-wall backing at these urinal fixture locations at Historic Structure and using a wall mounted carrier in lieu of a floor mount carrier. This would eliminate the need for existing floor/wall modifications to secure floor mount carrier. | See VBFA's response ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/16/2020 |  |  |  |  | Closed | 04/23/2020 | 04/30/2020 | 04/30/2020 | 04/30/2020 | 04/16/2020
400 |  | 0 |  |  | Request for Information | Instruction rm 208,209 Drape controls | Can we get shop drawings for the motorized drapes in instruction rm 208 and 209? Drawing XE112 note 13 is telling us to get the location for drape control J box from the architect. see attached drawing |  | this is a task for westland construction. shop drawings will come from the sub that installs the drapery and motors. ¦ ¦ This needs to be coordinated with the drapery installers. They will control the location of the boxes for motor controls. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/16/2020 |  |  |  |  | Closed | 04/23/2020 | 04/23/2020 | 04/23/2020 | 04/23/2020 | 04/16/2020
401 |  | 0 |  |  | Request for Information | CCD 047 Detail Clarification | Please confirm the highlighted cloud on the attached drawing are typos as discussed between David Adams and Matt McBride on the site on 4/16/2020. The details called out are on sheet S241 not S247. |  | please see response from ARW ¦ That is correct. The highlighted details should read 1/S241. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/17/2020 |  |  |  |  | Closed | 04/24/2020 | 04/23/2020 | 04/23/2020 | 04/21/2020 | 04/17/2020
402 |  | 0 |  | AD103, AD105, AE143, AE145 | Request for Information | Demolition Plan and Floor Plan Discrepancies | The demolition plans show removal of plaster on 3rd and 5th floor in various areas but the floor plans do not show any new finishes. Please advise that that only plaster will be replacing any demolished plaster for walls designated as "EXISTING WALL TO REMAIN." |  | This is part of upcoming CCD -58. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 04/20/2020 |  |  |  |  | Closed | 04/27/2020 | 05/18/2020 | 05/18/2020 | 04/21/2020 | 04/20/2020
403 |  | 0 |  |  | Request for Information | LVL 3: Men/Women Instruction Rooms and Corridor Ceilings | Men/Women Instruction Rooms on level 3 show ceilings to remain. These ceilings have been completely removed. Now that majority of duct-work is installed and we know that spacing will allow, please advise if it is acceptable to install 2" 18 ga stud joists for the hardlid ceilings ILO a suspended drywall grid system. |  | 2" stud joists are not acceptable. Provide suspended gyp. bd. ceiling system per drawings and specifications. Additional information regarding replacement of the demo items will be part of the upcoming CCD-58. Please coordinate accordingly. ¦ after further discussion with structural engineer we are not comfortable with a 2" or even a 2-1/2" stud spanning across these spaces and performing very well. Please provide the suspended gyp system as called for. ¦ ¦ I phrased my question wrong. It would not be 2" 18 ga, it would be 2-1/2" 18 ga. The reason we are requesting approval to use studs instead of a suspended hardlid with wires is because studs will ensure a level ceiling from corner-to-corner. Suspended wire ceiling have a tendency to create warranty issues (cracking). We are willing to use 2-1/2" 16 ga studs if necessary because we know they will provide a cleaner finish and require less maintenance down the road. Please advise. |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 04/20/2020 |  |  |  |  | Closed | 04/27/2020 | 05/28/2020 | 05/22/2020 | 04/22/2020 | 04/20/2020
404 |  | 0 |  |  | Request for Information | LVL 5: Instruction Room Ceilings | In the instruction rooms on level 5, now that majority of duct-work is installed and spacing will allow, please advise if it is acceptable to install 3-5/8" 20 ga stud joists ILO suspended drywall grid system. |  | Our drawings indicate that these rooms are already specified as 3-5/8" framed ceilings. Please install as specified. In the future RFI's need to be directed to Westland first. All RFI's are to be reviewed by the Westland team before forwarded to the Architect. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 04/20/2020 |  |  |  |  | Closed | 04/27/2020 | 05/18/2020 | 05/18/2020 | 04/20/2020 | 04/20/2020
405 |  | 0 |  |  | Request for Information | Level 2 Column Wrap | Is it acceptable to change the support bract at the top of the steel jacket on the 2nd floor from 29” to 18”? This question has arisen because the lower section of the bracket when installed at 29” is exposed at the bottom of the capital. When the bracket is installed at 18” it is enclosed in the capital. For reference I have attached a drawing provided by Fetzer’s. |  | This is acceptable to use an 18" dimension. We will include this revision in a forth coming CCD. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/20/2020 |  |  |  |  | Closed | 04/22/2020 | 04/21/2020 |  | 04/21/2020 | 04/20/2020
406 |  | 0 |  |  | Request for Information | CCD 047 Detail 11/S246 | 11/S246 has been added to the drawings, but it is unclear where this detail occurs. Please clarify |  | See response from ARW. ¦ CCD 045r1 was issued to Westland on 4/30/2020 ¦ That detail was inadvertantly added into the CCD047 set. It is now included with CCD45 and occurs where the steel beams for the east tower floors are connecting to the stone walls. Please see CCD45 for more information. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/27/2020 |  |  |  |  | Closed | 04/28/2020 | 04/30/2020 | 04/30/2020 | 04/22/2020 | 04/21/2020
407 |  | 0 |  |  | Request for Information | CCD 047 Barrel Ceiling Catwalk | Please see the attached drawings regarding CCD 047 for the barrel ceiling catwalks being installed to allow for access above the barrel ceiling. Please advise accordingly |  | please see response from ARW. a forthcoming asi will provide more information for the access doors. ¦ The highlighted note is correct. The intent with the new framing scheme was to completely remove from the project the existing beams that are NOT currently supporting the ceiling framing with 1x hanger pieces. Based on the current condition, it appears that approximately every other beam is NOT supporting the ceiling framing. Only the beams that are currently supporting the ceiling framing are to be replaced with the new LVL beams shown in the drawings. We are unsure what the question is for the ladder access. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/21/2020 |  |  |  |  | Closed | 04/22/2020 | 04/22/2020 | 04/22/2020 | 04/22/2020 | 04/21/2020
408 |  | 0 |  |  | Request for Information | Basement Capital Damage | During the installation of the C channel in the basement there was some damage found on the capital top between grid lines HC and HB on the Northside of the building. I have attached a marked-up photo and screen shot of sheet S102. |  | See ARW's response ¦ It will be acceptable to install the stub column as currently detailed but to only install the anchor bolts closest to the stone wall. The anchor bolt closest to the edge of the column capital can be omitted. Provide solid grout as required between the base plate and the remaining portions of the capital. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/21/2020 |  |  |  |  | Closed | 04/22/2020 | 04/28/2020 | 04/27/2020 | 04/22/2020 | 04/21/2020
409 |  | 0 |  |  | Request for Information | Purlin at Level 5 Elevator Infill | Is it acceptable to use this as an alternative to the (2) 2x12 @ 16" o.c. called out on sheet S105. If so, this would provide the room for the conduit bank as called for on sheet EP105. then in the area North of the new Purlin can go back to the design if wanted. |  | See response ¦ please see response from ARW ¦ The substitution request is acceptable to use the (4) LVL joist at the existing purlin location. An addition (3) LVL joist will need to be installed against the existing wall. Please use 2x6 T&G decking across the new framing. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/22/2020 |  |  |  |  | Closed | 04/22/2020 | 04/28/2020 | 04/27/2020 | 04/23/2020 | 04/22/2020
410 |  | 0 |  |  | Request for Information | North-West Baptistery Joists | During the installation of the C channels it was discovered that alongside of the Historical beam there is a layer of Plaster, a piece of 1x material with a 2x4 ledger then the Joist resting on the 2x4. I have illustrated the condition in the attachment. |  | See ARW's response ¦ Please install the channel beam tight to the underside of the bottom side of the 2x4 ledger. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/22/2020 |  |  |  |  | Closed | 04/22/2020 | 04/29/2020 | 04/29/2020 | 04/23/2020 | 04/22/2020
411 |  | 0 |  |  | Request for Information | Level 5 Barrel Roof Access Doors | Question Asked by Creg Norton via Email 4-21-20 @ 5:18 PM 1. Are the doors to be centered 2. Are the doors to be added to the north side 3. If yes to 1 & 2 plaster will need to be removed, and the doors opening cut in. Response given by Scott Gilberg via Email 4-21-20 @ 5:58 PM 1. Yes…..the design intent is that each of these access doors is centered within its own area. We will later provide a piece of art work that will be hung over the access panel as to hide the panel from view. 2. Yes, the same is to happen to the north side. 3. It is understood that some plaster will need to be demo’d as some of the access/openings may need to be shifted to be centered and others will be new altogether. Please confirm that the response above is correct. |  | the response given is correct. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/22/2020 |  |  |  |  | Closed | 04/23/2020 | 05/11/2020 | 05/08/2020 |  | 04/22/2020
412 |  | 0 |  |  | Request for Information | Recessed Kitchen Floor | Is the concrete way slab at the tile floor area in the Kitchen to be recessed to receive the ceramic tile? Sheet AE146 calls out the Kitchen slab elevation to be 87’-0”. |  | this information to be provided in a forth coming ccd |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/22/2020 |  |  |  |  | Closed | 04/29/2020 | 05/11/2020 | 05/08/2020 |  | 04/22/2020
413 |  | 0 |  | C.10, C.15 | Request for Information | Existing Waterline Electrolysis | Please advise if the existing water line between the water meter and the mechanical room should be exposed to verify no electrolysis existing. If electrolysis is found should be replaced and corrected. For Clarity I (David) have attached a photo showing the line in question. It is titled RFI - 413 EXISTING WATERLINE ELECTROLYSIS. |  | The Civil revisions for the waterline replacement will be on upcoming CCD-059. ¦ CCD-059 was signed and sent out 6-15-20. ¦ Attached is a drawing that should reflect the work to be desired for this. On the west side are two 2" water meters. There are two 2" poly lines that come from the water meters into an existing concrete vault. In that vault one of the 2" lines turns into a 4" line and connects to the building. The other 2" line turns into a 4" line and runs north to an irrigation backflow preventer. On the east side, the existing 1.5" water meter will be relocated. It will be placed approximately mid-block on 300 East. The 1.5" water meter will connect to a 3" line that will connect to an irrigation backflow preventer that is on the temple property. ¦ ¦ ¦ we can review this with the other RFIs. I think we really just need to know why it wont fit and by how much, but I could be wrong. ¦ We will leave this open until we receive CCD- 059.Thanks, ¦ Civil Page C.11 on CCD 59 only shows replacing a 2-inch water line to the Mechanical Room domestic. The main line for the temple is 4 inch in the mechanical room. The vault on the west side of the grounds has TWO 2 INCH POLY lines joining into one 4-inch ductile iron, that needs to be replaced. see attached |  |  | High | David Adams | Westland Construction, Inc. | Zac Givens | Westland Construction, Inc. | 08/03/2020 |  |  |  |  | Closed | 05/16/2020 | 09/22/2020 | 08/07/2020 | 08/13/2020 | 04/22/2020
414 |  | 0 |  |  | Request for Information | Finish Floor Elevations - Annex | Currently the top of slab elevation for the Annex at level 1 is at 100'-0". The flooring for the stairs is hardwood and is also at 100'-0" per the architectural drawings. Please clarify whether the concrete slab is to be at 100'-0" - as the steel is currently in fabrication. |  | Correct. top of slab, main level for annex is at 100'-0". and the stair area receiving wood should also be at 100'-0". please coordinate this with Westland crew. this information has been provided in great detail in an earlier RFI. ¦ because we are using a wood flooring system that is only 3/4" thick and is directly glued to the concrete slab.........we are providing the 100'-0" mark as TOP OF SLAB. This 'benchmark' needs to be applied throughout project for consistency. The only areas to see a 2" drop will be the sloped tile areas of restrooms. Even then, the bottom of concrete/metal deck shall be at the same height as areas adjacent. perhaps this needs to be discussed in a 15 minute meeting on site?? ¦ This is a different location so we just wanted a confirmation on the elevations. We have attached a marked up drawings showing what we are looking at. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/23/2020 |  |  |  |  | Closed | 04/29/2020 | 05/11/2020 | 05/11/2020 |  | 04/23/2020
415 |  | 0 |  | A2/AE4125 | Request for Information | Casework Rm 148A off of instruction Rm 2, room 148 A2/AE4125 | A2/AE4125 I have always seen the casework in the room off the large sealing room to be paint grade casework to match paint grade trim in the instruction room.Currently this casework is Stain grade. Should this casework be paint grade? |  | All Casework and trim in room 148a to be paint grade. Please remove any reference to stain grade. GHID ¦ ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 04/24/2020 |  |  |  |  | Closed | 05/01/2020 | 05/21/2020 | 05/15/2020 | 05/15/2020 | 04/24/2020
416 |  | 0 |  |  | Request for Information | Masonry Lift Verification | This RFI is to document a conversation between Carter and Zach. They concluded that we can lay CMU block in 8' lifts so long as we still grout the masonry in 4' lifts. |  | see response from arw ¦ Grouting in lifts that are any higher than 5'-0" must follow the highlift grouting procedures noted in Structural Note M.11 and M.12 |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/27/2020 |  |  |  |  | Closed | 05/04/2020 | 04/30/2020 | 04/27/2020 | 04/27/2020 | 04/27/2020
417 |  | 0 | 260573 |  | Request for Information | Coordination Study Calculations | The infinite bus method will need to be used. Is it acceptable to calculate from the HV transformer at the city substation or does the engineer prefer to calculate from the MV transformer at the site? |  | It is acceptable to calculate the fault current from the substation transformer. It is also acceptable to calculate from the service transformer on site if sufficient data from the substation transformer is not available. ¦ |  |  | High | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 04/27/2020 |  |  |  |  | Closed | 05/04/2020 | 05/05/2020 | 05/01/2020 | 04/27/2020 | 04/27/2020
418 |  | 0 |  |  | Request for Information | Modified detail 1/S243 | See foundation step at grid A2 in the annex. Per contractor direction it was requested to modify detail 1/S243 and add form savers for the 24" mat slab north of the temple at elevation 90'. This would allow an extra 2 feet in elevation for the earthwork contractor to work with as they dig out the jacket walls at the exterior of the temple. Please review attached sketches of detail 1/S243 and confirm this is acceptable. |  | see arw response ¦ Mat slab reinforcing will remain at 12"o.c. ¦ ¦ The proposed sketch is acceptable with exception to the form saver dowel spacings. Please see attached sketch for a mark-up of the required dowel spacings. ¦ See follow-up question from contractor ¦ With the form saver dowels being required at 9" o.c. spacing will that change the mat slab rebar spacing which is shown at 12" o.c. top and bottom on S100 and S100a noted between grids A1 and A2? |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 04/27/2020 |  |  |  |  | Closed | 05/04/2020 | 04/30/2020 | 04/29/2020 | 04/29/2020 | 04/27/2020
420 |  | 0 | 220000 | P099, P110 | Request for Information | Level 0 Kitchen wall CO | Drawing P099 and P110 indicates a 4" wall clean out rising up at south side of kitchen in what appears to be a 3 5/8 stud wall furr out at CMU wall near stair 1 in basement annex. Due to the nature of these walls and size of vent/waste piping, please advise if a floor clean out is desired in this location. | Allow for a floor clean out in this location or provide a notch in the CMU wall/wider furr out for wall clean out to be installed. | See upcoming CCD 054.2 for clarification ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/27/2020 |  |  |  |  | Closed | 05/04/2020 | 05/21/2020 | 05/15/2020 | 04/29/2020 | 04/27/2020
421 |  | 0 | 230000 | M411, M711 | Request for Information | Control Valves/Piping at Cooling Towers | Please review attached drawings M411, M711 and HVAC automated control valve schedule submittal page 115. Please clarify what the intended design is for the condenser return piping leaving the central plant chillers returning to the cooling towers. Various pipe sizes/valve sizes are shown. | Provide clarification of condenser piping sizing at cooling towers to allow for accurate CCD#28r1 pricing and final installation. | Please change the pipe sizing per the attached document "condenser schematic M711 edit VBF". ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 04/27/2020 |  |  |  |  | Closed | 05/04/2020 | 05/22/2020 | 05/21/2020 | 04/29/2020 | 04/27/2020
422 |  | 0 | 220000 | P113 | Request for Information | 4" waste pipe at level 3 Annex | Drawing P113, southwest corner of building indicates a 4" waste/vent pipe routing up to level 4. Please review attached drawings for clarification. | Please advise if this 4" piping is serving part of the plumbing system of if it can be removed from the model. | See VBFA's response ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/28/2020 |  |  |  |  | Closed | 05/04/2020 | 04/30/2020 | 04/30/2020 | 04/30/2020 | 04/28/2020
423 |  | 0 | 230000 | M402 | Request for Information | Missing Soffit Detail for Mechanical Install | Drawing M402, keynote 3 at spiral stair tower states to refer to architectural sheets for soffit detail. No detail for can be found. | Please provide a soffit detail for the ductwork at the spiral stair towers. | Please refer to CCD 070 for this detail which was sent out on 7.7.20. Thanks ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/28/2020 |  |  |  |  | Closed | 05/05/2020 | 07/09/2020 | 07/08/2020 | 04/29/2020 | 04/28/2020
424 |  | 0 |  |  | Request for Information | RE: RFI 164 Fountain Tile material | RFI 164 addressed the 2 x 2 tile but we need the same information on the 6 x 6 tile? |  | The 6"x 6" Tile will manufactured from the following source: Artistic Abode Tile Studio Christine Davidson 541-350-2727 16887 Covina Rd, Bend, OR 97707-2080 artisticabode@gmail.com An image of the mock-up the manufacturer has created is attached, however, final design and colors need to be approved prior to ordering. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 04/28/2020 |  |  |  |  | Closed | 05/08/2020 | 06/02/2020 | 05/28/2020 |  | 04/28/2020
425 |  | 0 | 230000 |  | Request for Information | Structural Sleeves for Mechanical level 3 and 5 | Per job walk and conversation with structural engineer of record, please confirm the use of schedule 40 steel sleeves as acceptable for the 10" mechanical opening required at level 3, room 317/319 and the 18" mechanical opening at level 5 barrel ceiling. Note that the openings are located below nearby joists. | Confirm suggested sleeves and locations are acceptable as requested. | Schedule 40 pipe is acceptable for use in the noted locations. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Structural Engineers |  | 04/28/2020 |  |  |  |  | Closed | 05/05/2020 | 04/30/2020 | 04/29/2020 | 04/29/2020 | 04/28/2020
426 |  | 0 | 250000 | M sheets | Request for Information | Wall HVAC Thermostat locations | It has been requested to vertically align the HVAC thermostats above the room light switches. May adjustable thermostats be lined up horizontally with light switches to meet ADA requirements? | Please advise preferred orientation and placement of the HVAC Thermostat for both ADA and Non-ADA compliant areas. Provide a detail indicating height and location preferred with light switch. | Please see sheet GA001 with all of the t-stats changed to be located above the light switches. The t-stats are a sensor type only and do not require adjustment and therefore do not need ADA access. The t-stats should be located 12" above the light switches center-to-center. ¦ Agree, align T-stat 12" above switches. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/28/2020 |  |  |  |  | Closed | 05/05/2020 | 05/22/2020 | 05/22/2020 | 04/29/2020 | 04/28/2020
427 |  | 0 |  |  | Request for Information | Missing dowels annex grid AB/A2 | See attached sheet S100 and photo. By mistake we interrupted the south footing step detail at grid A2 in the annex to end at the CW4 wall at grid AB. There is a small 2-3 feet of #5 bar at 9" o.c. that we will need to drill and epoxy. Is detail 8/S210 acceptable at this location to add the missing dowels? 19" embedment. |  | See response from ARW. ¦ ¦ Drilling the dowels per 8/S210 is acceptable. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 04/29/2020 |  |  |  |  | Closed | 05/06/2020 | 04/30/2020 | 04/30/2020 | 04/29/2020 | 04/29/2020
428 |  | 0 |  |  | Request for Information | Ceiling Joist Tie Wire | Please confirm that per the attached email dated 4-28-2020 that it is acceptable to use attached the tie wire under the ceiling joist instead of attaching it to the joist with an eye bolt. |  | See ARW's response ¦ The proposed attachment is acceptable. Please use the same wire gauge and twist the wire a minimum of 4 twist-turns around the vertical wire as shown in detail 9/S246. Please ensure that wires are tight when installed so to avoid movement and cracking of the plaster ceiling. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/29/2020 |  |  |  |  | Closed | 05/02/2020 | 04/30/2020 | 04/29/2020 | 04/29/2020 | 04/29/2020
429 |  | 0 |  |  | Request for Information | Roof Drain Locations | Would it be acceptable to install the roof drains in the location shown on the attached AE106 sheet? There are concerns that the roof cricket needed to get the slope for the roof drains as shown will rise the roofing material above the lowest portion of the battlements. In order to finish the roof drain piping we will need to get this answer back. This is applicable to the North and South sides on the East end of the roof. |  | Hey Dave, Did you mean to send this RFI to structural? I know you like keeping us on our toes with a bazillion rfi’s but this seems like more of an architectural and mechanical question. 😊😊 ¦ Dave, The location you are proposing will not work and conflicts with mechanical units that are part of an upcoming CCD. We recommend keeping the roof drains per the location on the construction drawings. Please see the attached image of the current model showing the roof lower than the embattlements. Please verify if and if still a problem we need to know where the discrepancy may be. ¦ per further discussion and review with mech engineers and GC, it has been determined that the locations of the existing roof drains can also be the location of the new roof drains. OF course an over flow drain will need to be added to each location. This also means that the roof cricketing can remain as currently configured. this will require careful coordination between the drain lines and the fan coil units that are just below the roof in this area. also keep in mind the can lights and sprinkler lines below. ¦ WOW... I was positive that I had the Mechanical Engineer. Sorry for the confusion. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/07/2020 |  |  |  |  | Closed | 05/03/2020 | 05/11/2020 | 05/08/2020 |  | 04/29/2020
430 |  | 0 |  |  | Request for Information | Roof Anchor Points | The new roofing material is going to be 6” in depth. This will result in most of the existing roof anchor points being under the roof. For reference I have attached photos. The manufacturer is looking for 12” exposed above the roofing membrane for warranty. This would result in the Anchor point being 18” above the roof structure and would allow for the proper roofing boot installation. Please advise |  | Per discussion on site with Scott Gilberg and David Adams, CRSA will need to determine if existing davits need to be replaced or can be reused. If new davits are required, the roof trusses will need to be checked for new davit loads and will likely need to be strengthened for the new loads. |  |  | High | Brad Bartlett | Broken Arrow Inc | CRSA ARCHITECTURE |  | 04/29/2020 |  |  |  |  | Closed | 05/02/2020 | 05/14/2020 |  | 05/01/2020 | 04/29/2020
431 |  | 0 |  |  | Request for Information | Roof Reinforcement for Lift | The Roofer has mentioned the possible need for additional reinforcement to be installed on the North side of the roof. This is resulting from the weight of the existing movable lift along with any load it may be used for. The roof construction consists of: 1. the roof structure, 2. 6” of Insulation, 3. 5/8” Densdeck, 4. roofing membrane. |  | see response from ARW. ¦ Please see notes made on the detail section of the roof assembly. this detail is acceptable, but needs to be extended to the roof ridge, as to avoid a 3/4" lip under the membrane where the plywood is terminated. ¦ As discussed on site, wood framing can be added in the layer of the insulation and additional sheathing can be included below the dens deck to help spread the load from the lift. When the new equipment is determined and the loads are known, this can be reviewed to come up with the best solution. ¦ Please update the response to note the system will be installed as; 1. Roof Structure 2. 6”Insulation 3. 5/8”Dens Deck 4. ¾” Fire Treated Plywood (only on the North side of roof) 5. Roofing Material |  |  | High | Brad Bartlett | Broken Arrow Inc | CRSA ARCHITECTURE |  | 04/29/2020 |  |  |  |  | Closed | 05/02/2020 | 05/28/2020 | 05/22/2020 | 05/01/2020 | 04/29/2020
432 |  | 0 |  |  | Request for Information | S.O. Cords to Roof Lights | It has been discussed on site that the S.O. cords providing power for the roof lights may need to be replaced with something more substantial. I have attached photos of the present condition of the cords to illustrate the concern. |  | We agree the SO cords need to be replaced. Per site visit discussion last week with Scott Hardy, we recommend stubbing conduit through the roof at each of the three light fixture rack locations on each side of the tower, to avoid having conduit or cords sitting directly on roof. Provide outdoor rated flexible conduit suitable for site location to properly protect wiring. Confirm that any damaged or improperly supported roof mounted lighting is fixed and supports reconstructed as needed, prior to re-install. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 04/29/2020 |  |  |  |  | Closed | 05/06/2020 | 05/07/2020 | 05/06/2020 | 05/06/2020 | 04/29/2020
433 |  | 0 |  |  | Request for Information | Confirm Additional 2nd Floor C Channels | Please confirm that per a site walk on 4-22-2020 the Owner wants the highlighted beams to get 2 channels as called out in Note 10 on this sheet. | Confirm | Per direction of the owner as of 05-07-20, the additional channels are NOT to be added. ¦ It is our understanding that Chris Robbins requested the remaining wood beams be upgraded with channels. These are not required structurally, but were requested for sake of consistency across the floor. Please verify with owner this is indeed what they want. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/02/2020 | 05/11/2020 | 05/08/2020 | 05/01/2020 | 04/30/2020
434 |  | 0 |  |  | Request for Information | 5th Hall Outlet Mounting Height | On the 5th floor in the South Hall we can mount the Outlets at 17” and on the North we can get 18”. Please advise if this is acceptable or if we should install them all at 17”. The reason for this height constriction is due to a beam installed in the wall holding the entablature up on the 4th floor. I have attached a drawing showing the affected areas. |  | Please install outlets at consistent heights, which appears to be 17" |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/06/2020 | 05/11/2020 | 05/11/2020 |  | 04/30/2020
435 |  | 0 |  |  | Request for Information | SW5 shear wall concrete reveal clarification | Reference sheets S254, AE203, AE146B, AE141A, AE142, AE143, AE144, AE145. Please answer the following questions so we can finish the formwork design for the west shear walls. 1) AE146B- what is the bump out in wall at grid HH between H2 to H3? Location clouded on attachment. 2) We assume the shear wall dimensions are typical from level 0.5 to roof being that there is not a slab and column plan beyond AE146B. Please confirm? 3) S254 shows a 15" unreinforced reveal in from level 1 to roof at the SW5 shearwall along grid HH. We will need clear dimensions to be able to form and pour this if intended to be concrete. Please provide dimensions. Or is the intent to have this reveal and surround detail achieved with fur out framing and plaster? |  | This bump out is to match the Historic East and West Facades. Field Verify the dimensions for accuracy Correct, there is no slab and column plan beyond AE146B. Shear wall should be 15" up to Level 2, then it can transition to 12" for Level 2-Roof Dimensions of this section of the SW5 Shearwall between buttresses should match the existing Historic West Facade. See attached images. Field Verify these dimensions for accuracy. Per continued Discussion, above Level 1 we can transition to Foam and stucco for the reveal on the 12" cast-in-place wall. It was indicated that the arch above Level 5 window would be easier to accomplish in Foam rather than concrete. Level 1 is to remain a concrete wall. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 06/10/2020 | 06/09/2020 | 04/30/2020 | 04/30/2020
436 |  | 0 |  |  | Request for Information | Plaster crown moldings | (Crown moldings on pg. AE571 detail E1 and E2) The beam crown, that is now made of plaster, will it be solid or hollow? Detail A1 on Pg. AE583 shows a the crown wrapping an existing beam. Are there two different scenarios (real beam, false beam)? If yes, I will need to make two different plaster molds to account for each. If you could get me this information ASAP that would be great. Thanks. |  | due to some construct-ability the millwork (crowns and other details on box beams) will need to be constructed from GFRG. This would be one location in the historic building where plaster crown molding is NOT used. ¦ |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/28/2020 | 05/26/2020 | 04/30/2020 | 04/30/2020
437 |  | 0 |  |  | Request for Information | C Channel Height Conflict | On levels 3 and 5 in the East center room we have about 6” between the top of HVAC cut out and the bottom of floor joist above. Right now, we are using a 15” C Channel that won’t be able to fit in these locations. For reference I have taken some pictures of the locations effected. |  | this issue should be resolved in CCD 37R.2 -should be issued today or Monday, May 11th. ¦ Refer to detail 6/S240. ¦ This was reviewed with David Adams on site and a new detail will be prepared and included in a forthcoming CCD for this condition. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 05/07/2020 | 06/04/2020 | 06/03/2020 | 05/01/2020 | 04/30/2020
438 |  | 0 |  |  | Request for Information | Plaster Medallions | What size of electrical conduit will be stubbed out of the medallions for the lights? I need to know the size so I can make a hole in the center. |  | 4" round box 2 1/8" deep ¦ This question came through and I thought you guys would be able to answer it without me needing to send it into the Arch. or Electrical Engineer. |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | Trask Johnson | Wilkinson Electric Inc | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/12/2020 | 05/12/2020 | 04/30/2020 | 04/30/2020
439 |  | 0 |  |  | Request for Information | Stair tower Plaster base board | Will you get me a profile and the dimensions of the base board molding that will be installed in the spiral stair towers? I need this information to create a plaster mold. |  | This is going to be changed to wood. ¦ |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 08/13/2020 | 07/27/2020 | 04/30/2020 | 04/30/2020
440 |  | 0 |  |  | Request for Information | Winding Stair Center Chase | Bottom of south stair tower is concreted in. Duct is 4’-7”; cylinder is 18”. Floor to concrete slab is 18”. Needs to go down to 4’-7” for roof drains. May be able to reroute roof drains another way? Slope for roof drains to get grade is the biggest concern. Dewatering systems and floor drains are under the slab… CLR asked Team to consider options for access. CLR also directed WCI to submit a RFI. | We are seeking responses from both the Structural and Mechanical engineers on this issue with CRSA then sending it back. | Based on what can be seen visually below the stair tower, it appears that the referenced concrete slab is actually a footing for the newer wood columns and beams that were placed below the stair towers. It appears that these were placed to help support the stair towers and prevent any further settlement. If it is necessary to cut this slab to install the roof drains, then new footings and support framing for the stair tower will be required in this basement area. Please advise what direction will be taken. ¦ we have attached an Additional Document for your consideration regarding this RFI. ¦ Please see the attached diagrams and responses that were a part of RFI #204. This seems to be referencing similar issues. ¦ please see attached detail from ARW in RFI #204 ¦ Our understanding is that the 4'-7" excavation under the stair tower is due to the roof drain routing. This was discussed with Westland and VBFA while on site 5/28/2020 and it was determined that the roof drain routing could be accomplished in a way that did not require the slabs below the stairs to be removed. ¦ Please confirm and verify pipe sizing and invert elevation? The attached was discussed with the design team onsite last week after shooting the elevations with Bob and Cobe. ¦ See response from the Structural and Mechanical engineers. ¦ ¦ ¦ RFI 204 is regarding the structure of the stair tower and the conflict with it when trying to run the Mechanical system up the center chase as shown on the drawings. RFI 440 referencing the duct that is 18” (20” with insulation) and the floor to top of concrete is 18”. Along with the roof drains that come through this area at 4’-7” below concrete. They are related in they are both related to the winding stair tower, but they are asking to different questions. ¦ ARWs response is not addressing the 4' 7" excavation under the stair tower that must pass through the concrete slab below. If we excavate this as shown on sheet P110A it could undermine the center support of the winding stairs. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/09/2020 |  |  |  |  | Closed | 05/03/2020 | 06/24/2020 | 06/15/2020 | 06/09/2020 | 04/30/2020
441 |  | 0 |  |  | Request for Information | Chandelier Mounting Brackets | Please provide a detail for the chandelier mounting bracket. The preexisting consisted of a carved wood block with a rope ran through it the toe nailed on to the 1X. When the new structure was being installed the framer pulled up on the block so he could run the tie wires and it was removed without much effort. |  | Use details 15/S244 and 16/S244 for chandelier's that are supported from new steel studs. For chandeliers that are supported from wood framing such as the chandeliers in the 4th floor, there are to be (3) new LVL's installed to support the chandeliers. See sheet S106 and Roof Framing Note #2 for the support of the new LVL's. The chandeliers and pully systems can be attached directly to the LVL's without the need for a plate unless specifically needed based on chandelier support requirements. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/07/2020 |  | 05/01/2020 | 04/30/2020
442 |  | 0 |  |  | Request for Information | Column interference at Ramp - Annex | Currently there is a steel column interfering with the ramp that was added at the west wall near AH between A3 & A4. Please provide direction as to how these two items coordinate. Currently GSW is planning to install the column with the rest of the Annex columns, but it appears the ramp is ready to be poured and this column may hold up progress. |  | CRSA has no preference to either of the options provided by ARW. please proceed as requested by ARW. ¦ ¦ As discussed with Carter Cluff, a new concrete pier will need to be added to provide a solid base for the column and the column will need to be shortened in order to place the ramp concrete as planned, or a blockout will need to be provided around the column base. Either is acceptable to structural but should be coordinated with CRSA. Please notify ARW if a new pier is requested so it can be detailed. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/07/2020 | 05/06/2020 | 05/01/2020 | 04/30/2020
443 |  | 0 |  |  | Request for Information | Annex Elevator Wall Heights | Currently the elevator walls are shown terminating at 116'-6". This will require the mason to notch the walls to allow beams / joists to run through. Please confirm thi is the intent. Also - as there is no positive connection to the roof decking, GSW has no embeds figured for this wall. Please provide information if this is to be different. |  | see arw comment referencing a detail for concrete lids over the elevators shafts that are in question. ¦ ¦ It was understood that a lid would be provided at the top of the walls at the elevator shafts. See detail 9/S231. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/05/2020 | 05/05/2020 | 05/01/2020 | 04/30/2020
444 |  | 0 |  |  | Request for Information | West Wall Beam Connections | The detail called out for the west wall connections (3 beams) denotes a notched wall condition (ref 20/S220). As this wall is already poured without notches - is it possible to utilize a connection similar to 17/S220 with a post applied flat plat in lieu of notching the wall? |  | See attached response/ connection detail from ARW. ¦ ¦ Please see attached sketch for beam to wall connections. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 04/30/2020 |  |  |  |  | Closed | 05/07/2020 | 05/05/2020 | 05/05/2020 | 05/05/2020 | 04/30/2020
445 |  | 0 |  |  | Request for Information | Foundation Wall Reinforcement | In the Historical Foundation Wall Reinforcement submittal review it was noted on the returned submittal that; “We did not review these drawings since there will be so many changes at the foundation jacket walls due to the recent discovery of the existing stone foundations.” Please provide the design changes associated with this scope of work as it is holding up the shop drawings of the rebar. |  | See CCD-049 per ARW's comment below. ¦ Information will be included in CCD049 |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/01/2020 |  |  |  |  | Closed | 05/04/2020 | 05/07/2020 | 05/06/2020 | 05/01/2020 | 05/01/2020
446 |  | 0 |  |  | Request for Information | Column Footing | In the submittal review it was noted on the returned submittal that; “Due to recently discovered existing conditions of column footings, the detailing of the new foundation may be revised in order to accommodate existing conditions.” Please provide the design changes associated with this scope of work as it is holding up the shop drawings of the rebar. |  | See CCD 049 for revised columns. ¦ Information for these columns will be issued in CCD049. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/01/2020 |  |  |  |  | Closed | 05/04/2020 | 05/07/2020 | 05/06/2020 | 05/01/2020 | 05/01/2020
447 |  | 0 |  |  | Request for Information | Catwalk on West of Historic | Please confirm that per a conversation on site we are to add a catwalk on to the West end of the historic Level 4 Ceiling Access. This catwalk is to mirror the catwalk in the truss bay to the East. |  | confirmed. please provide catwalk as described. |  |  | Medium | David Rockhill | Rockhill Construction | CRSA ARCHITECTURE |  | 05/01/2020 |  |  |  |  | Closed | 05/08/2020 | 05/11/2020 | 05/08/2020 |  | 05/01/2020
448 |  | 0 |  |  | Request for Information | Catwalk Conformations | Please confirm that per the site walk on 04-30-2020: 1. We can wrap the Tie Wire around the LVL similarly to how it is installed around the Ceiling Joist. 2. We are able to raise the access door 4” from its present location making it 7’6” off the floor in the hall. 3. We can install the latter accessing the Catwalk at the location where the latter rungs will clear the ceiling joist by 3/4” and tying in flush with the top of Catwalk. |  | Please see ARW's response regarding items #1 and #3. Item-#2 - access doors to be provided as shown in detail A5/AE556. install each access panel centered in each bay. please provide head heights at 7'6" above finished floor. ¦ ARW's can confirm items #1 and #3. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/01/2020 |  |  |  |  | Closed | 05/04/2020 | 05/11/2020 | 05/08/2020 | 05/04/2020 | 05/01/2020
449 |  | 0 |  |  | Request for Information | Field Report 11 | Please confirm that we are to do the work as outlined in the attached ARW Field Report. It is anticipated that there will be added costs to get the activities listed below done. 14-2 grout the joist pockets solid 14-3 new FRP wraps above all of the doors/ plaster be removed above all the remaining door locations 14-4 remove all loose stone 14-7 remove this chair rail and grout the created void solid For reference I have attached the field report and Highlighted the additional work activities in yellow. |  | please proceed as instructed by ARW. ¦ The items listed in our report are our professional recommendations for the owner to consider and implement into the project. Costs associated with those items should be addressed with the owner. If there are concerns then we are happy to have a conversation with the team. Item 14-3 is an area where we are looking at alternatives to the FRP. We would recommend holding off on that specific item until a firm direction is determined. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/01/2020 |  |  |  |  | Closed | 05/08/2020 | 05/07/2020 | 05/07/2020 | 05/01/2020 | 05/01/2020
450 |  | 0 |  |  | Request for Information | Door Hardware questions per meeting with architect 4-28-20 | See attachments for list of questions |  | Per meeting with Westland, CRSA, Fetzers, Allegion, & TFM, door hardware was discussed and revised. See CCD 104 for revised Door Hardware |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 05/02/2020 |  |  |  |  | Closed | 05/09/2020 | 11/10/2020 | 11/02/2020 |  | 05/02/2020
451 |  | 0 | 230000 | M102 | Request for Information | HVAC ceiling conflicts at 219, 220 and 221 | Drawing M102, vestibules 220 and 221 are shown four 24"x12" ducts routed to four SWS-1 grilles located in instruction room 219. It appears the ceiling at these locations does not allow for sufficient height to install as drawn. See attached screen shots showing the conflict between ceiling heights, crown moldings and duct. | Please advise what means can be followed to install this duct as shown. Possible duct size change? | Sawcut the opening to accommodate the design duct size. Angle the sawcut to accommodate the larger grille. See CCD37R.2 detail 6/S240 for structural support. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 05/04/2020 |  |  |  |  | Closed | 05/11/2020 | 05/22/2020 | 05/21/2020 | 05/05/2020 | 05/04/2020
452 |  | 0 |  |  | Request for Information | Existing South West Annex Wall | The existing foundation wall on the South West corner of the Annex along grid A2 is 5" too far to the West. I attached a sketch that Scott, Chris, Carter and Judd talked about on Friday. Please confirm we are to use the existing foundation wall layout and make the necessary changes to the precast to make it work. I also attached information on the precast panels. |  | the existing foundation wall at the south corner at grid A2 is 5" further to the SOUTH than originally anticipated. please proceed with foundation wall layout /design. this will necessitate an additional 5" of length be added to pre-cast panel 'L' and a 5" reduction to panel 'E'. Westlan/CRSA to coordinate these revisions with Forterra. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/04/2020 |  |  |  |  | Closed | 05/08/2020 | 05/05/2020 | 05/04/2020 |  | 05/04/2020
453 |  | 0 |  |  | Request for Information | 4" Curb at Elevator & Xypex Waterproofing | Per the owner direction in the field please see the attached changes. We added a 4" curb wall at the Annex elevator pit footing for waterproofing at rough surface. Added Xypex to concrete around the annex basement existing mat slab elevator | This is a confirming RFI to track the pricing for this field direction. Work has already been completed. | work done is duly noted. |  |  | Low | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/04/2020 |  |  | 4860.00 |  | Closed | 05/14/2020 | 05/21/2020 | 05/19/2020 |  | 05/04/2020
454 |  | 0 |  |  | Request for Information | Level 4 Ceiling Elevation at North and South Sides | AE124 calls for the north and south ceiling elevations of level 4 to be at 17’ 3”. Per onsite conversation with CRSA, the ceiling will be lowered to accommodate mechanical and electrical rough in. See attached photo of existing conditions and advise what the ceiling height is to be. |  | Information regarding the ceiling changes for this area will be part of upcoming CCD-51. ¦ Please disregard comment for CCD-051. This is actually addressed in CCD-058. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/16/2020 |  |  |  |  | Closed | 05/16/2020 | 06/24/2020 | 06/17/2020 |  | 05/04/2020
455 |  | 0 |  |  | Request for Information | RCP01 Pump to Remain | Note 18 on PD100 calls for existing RCP01 to remain. There is concern that when this pump comes back online the seals will be cracked and it will need to be rebuilt. The pumps existing condition already shows evidence of leakage. Please advise if we are to rebuild or replace. Also, please advise if it is acceptable to relocate to the floor slab per TFM request rather than to go back in the air. Reference sheet MPD100 and M100. There is concern that the two existing CWP01 pumps and the existing CHWP-2 that are to remain will have cracked seals when they come back on line and will need to be rebuilt or replaced. Please advise if there is a preference or how you would like us to proceed. |  | Please provide a price to replace RCP-01, CWP-01 and CHWP-2. ¦ Please provide final pricing for acceptance. ¦ I have attached the pricing that was requested. ¦ The drawings will be updated as part of CCD-028 R.3 to show these pumps as being replaced. ¦ ¦ ¦ I will close this with the issuance of the CCD. |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 07/29/2020 |  |  |  |  | Closed | 05/11/2020 | 10/08/2020 | 08/12/2020 | 07/08/2020 | 05/04/2020
456 |  | 0 |  |  | Request for Information | Level 5 Chandelier Layout | Coming from east to west, Bay 1: there is not one Bay 2: 15 1/2" off edge of beam Bay 3: 72 1/2" " " Bay 4: 135 3/4" off edge of beam and 1 1/2" from the beam on the west side of bay Bay 5: None Bay 6: 53" Bay 7: None Bay 8: 9 1/2" For reference I have marked up a drawing showing the locations of the Chandeliers in Red Circles and possible locations of (3) 1 ¼” x 9 ¼” LVLs in yellow blocks. |  | please see response from arw ¦ Provide (3) 1-3/4" x 9 1/4" LVL's at each chandelier support location that is not located directly below an existing wood truss. |  |  | Medium | David Rockhill | Rockhill Construction | CRSA ARCHITECTURE |  | 05/04/2020 |  |  |  |  | Closed | 05/11/2020 | 05/07/2020 | 05/06/2020 | 05/05/2020 | 05/04/2020
457 |  | 0 |  |  | Request for Information | Furr out West Wall of Janitor Storage 004 | At the janitor’s closet in storage 004 the sink is called to be located against the west wall of that room which is an existing concrete wall. Should this wall be furred out to accommodate the plumbing for that sink? Furring out the wall would also help cover the existing wall, called to be painted, but which is unfinished condition. |  | No furring, this will be clarified in CCD 054 ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Camron Walker | Westland Construction, Inc. | 05/04/2020 |  |  |  |  | Closed | 05/11/2020 | 05/20/2020 | 05/15/2020 | 05/20/2020 | 05/04/2020
458 |  | 0 |  |  | Request for Information | Levels 3 and 5 Restroom Sizing | Please advise the size of the restrooms in the historical building on level 3 and 5. On Sheet AE143 it is calling out for the restrooms to be 10’. On Sheet AE145it is calling the restrooms as being 9’-6”. We need to know which one is correct or if we need a new size. |  | per on site discussion it has been decided that 9'-6" restrooms located on the 5th floor is the desired dimension for the 5th and 3rd floor restrooms. in a forthcoming CCD the 3rd level restrooms will be revised to reflect the 9'-6" dimension. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/04/2020 |  |  |  |  | Closed | 05/11/2020 | 05/07/2020 | 05/06/2020 |  | 05/04/2020
459 |  | 0 |  |  | Request for Information | Missing Sheet S204 | Detail 8/S241 references S204 which doesn’t exist. Please advise. Also, this same detail 8/S241 shows the micropile but is not clear on how they interact with the new concrete at the elevator slab. Please advise. |  | The reference to sheet S204 is incorrect and should reference detail 1/S242. This correction has been made in CCD49. The micropile interfaces with the concrete slab through a cap. Please provide a pile cap per the attached detail. This will be incorporated into the drawings in a forthcoming CCD. ¦ See ARW's response |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/05/2020 |  |  |  |  | Closed | 05/11/2020 | 05/20/2020 | 05/15/2020 |  | 05/05/2020
460 |  | 0 |  |  | Request for Information | Beam to Column Connection - Level 2 Historic | At Grid HC between grids H3 & H4 there is a new beam (W14x34) denoted. There is no attachment detail for this beam as it connects to the central stone column at H4 (see attached sketch for clarification). The North end of this beam attaches to a new HSS column per 17/S212 - please provide direction for the South end of the beam. |  | Please provide an L8"x8" bearing seat that is welded to the steel collar wrapping the tops of the stone column. See attached for a sketch of that detail. This detail will be included in CCD37-R.2. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 05/05/2020 |  |  |  |  | Closed | 05/12/2020 | 05/11/2020 | 05/07/2020 | 05/05/2020 | 05/05/2020
461 |  | 0 |  |  | Request for Information | LVL Floor Joist Header Fix | We are trying to keep the job moving forward and I need a fix for the holes in almost every floor from past renovations. A possible fix we could use on all floors is to remove the existing header [2] 2x6 and hanger with a new LVL header and new hanger with a new LVL to extend across the existing framed out opening. We would also like to have a common fix for all broken joist in the building to sister an LVL alongside at our discretion. I need this answer fast. For Clarification I have attached an example of what we are thinking of doing. |  | See response from ARW. ¦ See attached for infill framing and for framing at new openings in joist. For joist that are broken, please remove broken joist and replace with a new LVL joist that matches the depth of the existing joist. If removal of the joist is not possible then it is acceptable to sister the new LVL joist to the existing joist. |  |  | High | Creg Norton | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/05/2020 |  |  |  |  | Closed | 05/08/2020 | 05/20/2020 | 05/18/2020 | 05/05/2020 | 05/05/2020
462 |  | 0 | 230000 | M102 | Request for Information | SA dampers serving projector rooms | Drawing M102, stair lobby 201, is shown to install three (3) 10"x4" supply ducts serving three (3) projector rooms. Keynote #8 indicates to balance these locations at 100cfm each. The ducts are medium pressure with manual volume dampers. See attached drawing detail for clarification. Please advise if installing manual dampers at these locations is correct or if the manual dampers are to be control dampers with flow rings or VAV's in order to maintain the 100cfm. | Due to AHU constant volume and variable CFM flow, please advise if 100CFM is the desired level of balance for each outlet. If so, clarify if the manual damper is sufficient to control CFM requirement or if control damper/VAV is necessary. | Please install manual balancing dampers with remote actuation similar to Ruskin model ZPD. VAVs or other flow measurement devices are not required. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 05/05/2020 |  |  |  |  | Closed | 05/12/2020 | 05/22/2020 | 05/21/2020 | 05/07/2020 | 05/05/2020
463 |  | 0 |  |  | Request for Information | Framing Support for Exhaust Fans | Reference sheet M106A, AE106. Please advise if there is any framing support required for exhaust fans EF5-01 and EF5-02 on the Historic roof. There does not appear to be a detail in the structural drawings requiring any framing support at this location. |  | See response from ARW. ¦ Provide 2x6 below the roof on each side of the exhaust fan. The 2x6 on the east and west sides of the exhaust fan can run between purlins and be connected to the purlins with a Simpson U26 hanger. ¦ |  |  | High | Jason Fullmer | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 05/06/2020 |  |  |  |  | Closed | 05/16/2020 | 05/20/2020 | 05/18/2020 | 05/20/2020 | 05/06/2020
464 |  | 0 |  |  | Request for Information | Confirming RFI following Scott Hardy site visit 04/30 | Attached is a list of confirming items resulting from the site visit on 4/30 with Scott Hardy. |  | See attached document with responses to questions document. ¦ We are requesting night lights be installed throughout the building. We have several departments (Facilities, Security, Custodial, and Laundry) who access the building in the late evening, throughout the night, and early morning when the temple is closed. Most of our departments come in at different intervals, with one of them expected to work throughout the entire night. There is a need for these areas to be continuously lighted during this time for those required to accomplish their work without having to turn the main lights on and off continuously. Our recommendation is to install these night lights strategically throughout the building. This would help us provide a safer and more efficient way of accomplishing their essential work. ¦ ¦ Brian, Attached is the RFI Jason talked to you about regarding the night lighting. Please advise as to what your night lighting needs are. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Brian Chandler | CORPORATION OF THE PRESIDING BISHOP OF THE CHURCH OF JESUS C | 05/13/2020 |  |  |  |  | Closed | 05/13/2020 | 05/15/2020 | 05/14/2020 | 05/14/2020 | 05/06/2020
465 |  | 0 |  |  | Request for Information | Ground lights at stairs | Please provide a detail for the exterior lights at the stairs on the North/East corner of the Addition. Please reference the attached drawing showing the location. |  | New locations (1’-0” North of the Stair Wall) were coordinated with CRSA. Revised location will be issued in future CCD. ¦ These changes were issued as part of CCD-044R1 on sheet ES202. ¦ ¦ Please provide the CCD #. Thanks. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 05/06/2020 |  |  |  |  | Closed | 05/13/2020 | 06/24/2020 | 06/16/2020 | 05/07/2020 | 05/06/2020
466 |  | 0 |  |  | Request for Information | Existing parking lot lights | The existing parking lot lights are 1ph. 480V. diversified over 3 circuits (A-B, B-C, C-A), this would need to be a 3-pole breaker, these circuits will work for the parking lot lights. However, they are on a single pole relay we will either need to add a 3-pole relay or a 3-pole lighting contractor with the coil being powered thru the relay designated. The new lights on temple side of street which are 277V. would need to be powered by a different circuit and relay Please Advise. |  | We will adjust the circuits for the street lights and the control relay to be 3-pole in CCD-044. The relay is currently on LCP-A2B-13. We will split it up over LCP-A2B-13, 14, 15. ¦ Revised plans will be issued as part of CCD-044r2. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 06/25/2020 |  |  |  |  | Closed | 05/14/2020 | 07/13/2020 | 07/08/2020 | 07/09/2020 | 05/07/2020
467 |  | 0 |  |  | Request for Information | Superplasticizer dosage | In reviewing the concrete walls onsite with Matt with ARW on 5/7 we would like to have the option to add a full dose of super instead of a half dose that we had previously submitted. Please confirm discussion that we are ok to increase to a full dose to get our slump to a 9" if needed in walls. Submittal attached for reference. |  | Confirmed |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 05/07/2020 |  |  |  |  | Closed | 05/14/2020 | 05/14/2020 |  | 05/13/2020 | 05/07/2020
468 |  | 0 |  |  | Request for Information | EIFS Shapes | Will you send me some dimensions on these foam shapes for the battlement parapet detail D1, Roof parapet detail D3, and Parapet detail A1 on page AE508 |  | The intention of these profiles/ details for the west addition is for the Contractor to field verified and to match the existing battlements and buttress of the historic building. A profile template will need to be made that best matches the majority due to any variations between elements. ¦ |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 05/07/2020 |  |  |  |  | Closed | 05/14/2020 | 05/20/2020 | 05/19/2020 | 05/11/2020 | 05/07/2020
469 |  | 0 |  |  | Request for Information | Transom Windows above doors Lvl's 3 and 5 | Confirm glass transoms will be built the same way as existing transoms with individual panes of glass and glazing putty to hold glass in place. Glass and glazing putty is by the glass vendor. Current windows the wood window mullion protrudes from the face of the glass on the hallway side by 1/4" and glazing putty is holding the glass in place. See photos |  | New glass transoms shall be constructed similar to existing historic ones with 6 individual panes of glass (true divided lite). New transoms are to have wood in lieu of putty, existing shall remain putty. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 05/08/2020 |  |  |  |  | Closed | 05/15/2020 | 05/20/2020 | 05/15/2020 | 05/11/2020 | 05/08/2020
470 |  | 0 |  | WF310 | Request for Information | Fountain Piping into Mechanical Rooms | Sheet WF310 shows the water feature piping for the East Fountain running through the area wells on the east side of the annex into the equipment room (see attached). The General Contractor has informed us that the water feature piping cannot run through the area wells. Please provide us with direction how this piping is to be routed. Additionally, please provide us with elevations for the penetrations for this piping into the annex for both fountains, so we can coordinate with the concrete contractor to have them provide rebar windows in the concrete for our penetrations. Also, please provide elevations for the piping at both fountains. |  | Please see the attachments and responses below. ¦ |  |  | High | Tim Maynes | Stratton & Bratt Landscaping | CRSA ARCHITECTURE |  | 05/08/2020 |  |  |  |  | Closed | 05/15/2020 | 05/20/2020 | 05/19/2020 | 05/11/2020 | 05/08/2020
471 |  | 0 |  |  | Request for Information | Elevator rough opening west tower room 053 | Reference G/S304 and AE4018 1)The structural plans show one big opening for the double elevator. The architectural plans show 2 openings for the plan. Please provide direction? 2) Please confirm that we are to use detail 3/S222 to reinforce the headers above the openings at this location. No beam call out required. 3) Please confirm the jamb columns at this location are to follow 1/S201. |  | The center wall dividing the elevator shaft will be a metal framed wall not concrete. See also attached response from ARW. ¦ ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 05/11/2020 |  |  |  |  | Closed | 05/18/2020 | 05/20/2020 | 05/19/2020 | 05/19/2020 | 05/11/2020
472 |  | 0 |  |  | Request for Information | Dimension clarification grid A1 shearwall | Reference AE146, AE147, S102, C/S301 Please see questions marked on attached sheets. 1) Clarify east dimension of grid A1 shear wall 2) Clarify C/S301 east portion of shear wall appears to be labeled incorrectly. From level 100 above and east of grid AB we should have precast not cast in place concrete. Reference AP101. 3) Clarify west dimension of grid A1 shear wall. See AE146, AE147, S102 and C/S301 |  | East Edge of Shear wall aligns with Grid AB Correct - Above 100'-0" East of Grid AB is a Precast Panel Level 0 - West Edge of Shear wall is 4'-6" west of Grid AE Level 1 - West Edge of Shear wall is 6" west of Grid AE ¦ See CCD49-R.1 for an adjusted wall elevation C/S301. Refer to the architect for dimensional information of the wall extents. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 05/12/2020 |  |  |  |  | Closed | 05/19/2020 | 05/22/2020 | 05/22/2020 | 05/21/2020 | 05/12/2020
473 |  | 0 |  |  | Request for Information | Leak Detector at Chiller Room | At Mechanical Room 035, the leak detection for the chillers is not functioning anymore and will need to be replaced as part of the requirements for start up on the chillers. Please advise if we are to provide a new leak detector and provide specifications for what is wanted. |  | Please provide a price to replace the refrigerant leak detector. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 05/13/2020 |  |  |  |  | Closed | 05/20/2020 | 05/22/2020 | 05/21/2020 | 05/14/2020 | 05/13/2020
474 |  | 0 |  |  | Request for Information | Annex Stair Materials / Configuration | Current Details in the architectural sheets refer us to the structural drawings in reference to structural sizing of stringers / treads at Annex stairs (ref details AE509 & AE510). There are no materials given on any structural sheets to our knowledge. We are assuming C12x20.7 stringers with 12 Ga Bent Plate Treads. Please confirm this will be acceptable (see sketch for configuration). |  | These stairs are listed as a deferred submittal in Structural Note W.3.b. However, we would anticipate a C12x20.7 stringer and 12 ga stair pan to be sufficient. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 05/13/2020 |  |  |  |  | Closed | 05/20/2020 | 05/20/2020 | 05/18/2020 | 05/14/2020 | 05/13/2020
475 |  | 0 |  |  | Request for Information | All M.E.P. Layout | Would you please provide a location for all the M.E.P. (Walls, Ceiling and Floors where applicable) that is not addressed in RFIs 456 - Level 5 Chandelier Layout and 309 - Room Layout Consistency. This RFI has arisen out of a concern for the finish layouts for the trims and the gold leafing associated with the rooms. Please provide the rough dimensions from rough framing to rough framing. |  | Please refer to ASI #10 showing dimensions to the typ. layouts for level 3 and level 5. Contractor needs to verify existing rough openings and refer to door schedules and door details along with other information that has been previously given in CCD-19. Architect will be providing dimensions to the LVL walls in an upcoming ASI. Refer to sheet AE553 for gold leafing locations. ¦ See the attached revised LVL dimensioned layout at baptistry. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Kyle Welch | CRSA ARCHITECTURE | 09/11/2020 |  |  |  |  | Closed | 05/20/2020 | 12/17/2020 | 12/14/2020 | 09/18/2020 | 05/14/2020
476 |  | 0 |  |  | Request for Information | Exception for MC cable | Can we be allowed an exception to run MC cable(10 to 15') at several locations on level 5 (see attachment ) there is a structural beam preventing us from running conduit. |  | MC cable is acceptable for those locations. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 05/14/2020 |  |  |  |  | Closed | 05/21/2020 | 05/20/2020 | 05/19/2020 | 05/18/2020 | 05/14/2020
477 |  | 0 |  |  | Request for Information | Waterproofing on West & North Existing Annex Walls | Would you like us to waterproof the West and North existing Annex walls down to the bottom of the mat footing? Please advise. |  | Yes, the intent is to waterproof the exterior side of the existing west and north walls. In the bid set drawings there are some references calling for the waterproofing of the north wall, while it appears there is not such for the west. Please provide the water proofing along all portions of the west wall until reaching the existing mech room, where the new waterproofing will tie into the waterproofing of the existing mech room. Please follow the waterproofing details provided on Sheet AE502. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/14/2020 |  |  |  |  | Closed | 05/21/2020 | 05/21/2020 | 05/15/2020 |  | 05/14/2020
478 |  | 0 |  |  | Request for Information | Wood Truss Coordination - Steel | In the Historic Temple - Level 4 Truss Framing - we are attempting to coordinate the detail shown on 2/S240 which requires "straps" to be placed at 16" centers on the wood columns. The wood truss interferes with this spacing and the lattice won't allow for this to happen as designed. Please advise. |  | It is acceptable to only install the straps at the locations between the lattice members so they don't interfere with those members. Please do not cut any lattice or truss members for installation of those straps. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 05/14/2020 |  |  |  |  | Closed | 05/21/2020 | 05/20/2020 | 05/19/2020 | 05/18/2020 | 05/14/2020
479 |  | 0 |  |  | Request for Information | relocate Data conduits historic roof | Confirming RFI that as per Scott Gilberg 5/14/2020 we are to relocate data conduits on the historic roof south toward peek to allow access for window washing jib (see attachment) |  | this proposal is acceptable and confirms an onsite decision regarding such ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 05/15/2020 |  |  |  |  | Closed | 05/22/2020 | 05/22/2020 | 05/22/2020 | 05/18/2020 | 05/15/2020
480 |  | 0 |  |  | Request for Information | Exterior tower lights at historic roof | Follow up to envision engineering comments on RFI 432, we suggest a 1.5" rigid post at each corner of the light structure to support kickers off of rather than off of stone walls 10' away like currently done (they have fallen free and are attached to nothing now) we feel this will be more permanent and less likely to be damaged by roof traffic. |  | The proposed mounting described sounds good, but please send us a drawing (preferred) or sketch (acceptable) for review. David Tibbitts Envision Engineering ¦ This RFI is outside the scope of ARW's work. If structural guidance is needed, we are happy to help, but this direction needs to be given to us through CRSA. ¦ Is the intent to penetrate the roof with the mounting/support structure and power feed? If so, can the roof penetrations be made permanently water-tight? Our concern is that these fixture mounting structures will move in the wind and weather, and this could lead to the seal failing and water coming in through the penetrations. David Tibbitts Envision Engineering ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Jason Fullmer | Westland Construction, Inc. | 05/28/2020 |  |  |  |  | Closed | 05/25/2020 | 06/16/2020 | 06/10/2020 | 05/22/2020 | 05/18/2020
481 |  | 0 |  |  | Request for Information | CCD 54.1 Dimensions | CCD 54.1 shifts a column to the North from its original position. Please provide the dimension this column is to shift (see sketch). Thank you. This is along Grid AD and South of A7. |  | This column shifted North 5' - 8 1/2". See attached AE146 for revised dimension, center of column is 6'-0" South of GRID A7 ¦ CRSA will need to provide this new column location. |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 05/19/2020 |  |  |  |  | Closed | 05/26/2020 | 05/22/2020 | 05/22/2020 | 05/21/2020 | 05/19/2020
482 |  | 0 |  |  | Request for Information | CCD 54.1 Connections | The beams that connect to the new beam added in CCD54.1 have already been fabricated for a column connection. The typical notched connection would result in new beams being made. Is it possible to provide an extended shear tab type connection for these (2) beams (they are the W16x50 and W14x22 running East & West -see sketch for recommendation). |  | See attached for an acceptable connection. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 05/20/2020 |  |  |  |  | Closed | 05/26/2020 | 05/22/2020 | 05/21/2020 | 05/20/2020 | 05/20/2020
483 |  | 0 |  |  | Request for Information | Foundation Break Near A1 | We would like to pour a portion of the mat footing to be able to install the wall on grid A1 before the needle beam assembly installation. See the attached detail for clarification. Please advise on the minimum distance from the wall this mat footing break can occur. |  | Please keep a minimum distance of 12" away from shear wall. The mat slab bars that cross this construction joint will need to be fully developed either by a lap splice or using form saver dowels. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Structural Engineers |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 05/21/2020 | 05/20/2020 |  | 05/20/2020
484 |  | 0 |  |  | Request for Information | CC1 columns and intake well dimensions at grid A2 | 1)Reference RFI 452. With the existing south annex wall along grid A2 being approximately 5" south of grid A2 the north/south dimensions to the 24" CC1 columns will need to be adjusted. Please provide direction 2) The CW2 intake well walls between grid A1 and A2 and west of grid AF have a relief vent (RL3) that is 100" wide by 96" tall. With the existing wall being around 5" south of grid A2 do the wall dimensions need to be adjusted or shift to fit? The CB-4 beams and horizontal wall rebar shown on S100B will need to be adjusted to match the required dimensions if necessary. |  | The CC1 column must stay the same size so the location of the column will need to shift the 5" in order to maintain the same size. The size of the intake well must stay the same also so it will need to shift as noted by CRSA. The CB4 beam rebar should not be affected by this shift since the size of the area well is to remain the same. ¦ See responses below ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 06/01/2020 | 06/01/2020 | 05/20/2020 | 05/20/2020
485 |  | 0 |  |  | Request for Information | Roof Stucco Repair | Please advise if the attached detail will be adequate for repairing the sections of plaster that have been removed during the abatement process on the roof. |  | this approach and proposal is acceptable |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 05/22/2020 | 05/22/2020 |  | 05/20/2020
486 |  | 0 |  |  | Request for Information | Roof Kicker Stone Wall Interference | Please confirm is it acceptable to install 3-2x12 adjacent to the existing stone walls that are landing Just off set from center of the top battlement? This condition occurs at 2 locations 1 on the North and 1 on the South. |  | This is acceptable. Please rotate the kicker brace slightly so that it connects in the center of the stone battlement. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 05/22/2020 | 05/21/2020 |  | 05/20/2020
487 |  | 0 |  |  | Request for Information | Site sidewalk/paving sealer spec | It is being requested that we seal the sidewalks due to concerns that the aphids are falling from the pecan trees and staining the concrete. What sealer does the owner/design team want used on the sidewalks? The specification in division 03 3010, 03 3000, and 321313 do not have a specific product listed. The product we submitted on in submittal 323213.01 is Spec Chem 25 UV Cure and Seal. The cure we submitted on is WR Meadows 1100 and has already been applied and is taking some time for the membrane to break down so it would have to be stripped to be sealed earlier than we anticipated. Please advise on how we should proceed and what sealer we should procure and submit on. |  | See Comment from Melissa Fryer. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 07/09/2020 | 07/09/2020 | 05/20/2020 | 05/20/2020
488 |  | 0 |  |  | Request for Information | Confirm Roof Termination | Please confirm that the roof can be terminated as shown in the attached drawing and that we are to replace the 1”x1” with a pressure treated 2x12. |  | this approach is acceptable and confirms the decision had on site. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 05/20/2020 |  |  |  |  | Closed | 05/27/2020 | 05/22/2020 | 05/22/2020 |  | 05/20/2020
489 |  | 0 |  |  | Request for Information | 5th Floor Ceilings | Currently, the existing furring and plaster are at roughly 9'-3" high. This is what the finished ceiling height is called out as on the reflected ceiling plan. We won't be able to attach the bottom screw on our track because of how far off the wall the plaster furring is. We recommend wood ledgers be added above the furring wall to allow us to attach our track. Please advise. |  | Next time you or Mike are out I would like to review this question with you. It just seems a little open ended. What I mean by that is what floors are you referring to level 5 or throughout the project? ¦ I'll have Mike Yaksick get with you on it. |  |  | Medium | Aaron Bowers | Pete King Commercial | Westland PE’s |  | 05/21/2020 |  |  |  |  | Closed | 05/28/2020 | 06/16/2020 | 05/28/2020 |  | 05/21/2020
490 |  | 0 |  |  | Request for Information | glass at transom doors 208, 209, 210 | Will the glass at the transom in these doors be obscured glass. These door are to the instruction rooms and have the camera above the headers? If glass is obscured there should be no need for inset panels and trim in the radius jamb since this will not be seen. |  | will you please advise if it is 201 or 210? ¦ Yes, the glass will most likely be opaque. Correct there is No need for inset panels and trim in the radius head jambs. ¦ Door 208 209 210 |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 05/21/2020 |  |  |  |  | Closed | 05/28/2020 | 06/04/2020 | 06/03/2020 |  | 05/21/2020
491 |  | 0 |  |  | Request for Information | Addition Basement wall Demensions | Could we be provided with wall dimensions for Electrical Rm. 040 (see attachment) |  | See revised AE140 will requested dimensions ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 05/26/2020 |  |  |  |  | Closed | 06/02/2020 | 06/03/2020 | 06/03/2020 | 05/28/2020 | 05/26/2020
492 |  | 0 |  |  | Request for Information | Priesthood room speakers | Speakers are shown to be exposed on columns in priesthood room. Installing the conduit for speaker cable through the solid, plaster column capitals and beams resting on them isn't feasible. Can they be relocated to be recessed in ceilings (see attachment)? | Possible optional installations include: 1- Mounting the speakers horizontally up tight to lower ceilings next to the quatrefoil columns on North and South sides. 2- Recessing the speakers into the stone walls behind and above the Melchizedec pulpits on the East end. 3- Installing multiple recessed, directional speakers in lower ceilings and/or barreled ceilings. (See Attachment) | AV design for priesthood room to remain as shown. It has been confirmed with Church AV and ceiling speakers will not be acceptable”. Please provide additional details on why conduits and wiring cannot be concealed. Other than possibly short sections of concealed speaker whip cabling by the speaker, the main run of conduit and wiring will need to be concealed. ¦ Please refer to CCD-082 for the revised speaker locations and details. ¦ ¦ This has been reopened as a way for Trask to provide some suggestions to Scott. Resulting from a conversation that happened on site. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 07/29/2020 |  |  |  |  | Closed | 06/02/2020 | 08/25/2020 | 08/24/2020 | 07/29/2020 | 05/26/2020
493 |  | 0 |  |  | Request for Information | Historic bottom of jacket wall clarification | Please verify the following from meeting held with Westland, CRSA (Scott), ARW (Zach) and Innovative on 5/26/20: 1) North interior jacket wall section 1/S243- interior side bottom elevation of jacket at sloped slab was discussed at being at elevation 89'-6". 18" below top of sloped slab. This was determined based on RFI 182 which clarified the top of slope slab to be at elevation 91'-0". With the top of needle beam being at elevation 90'-0" the top of sloped slab at elevation 91'-0" the detail does not scale to reflect these elevations. Please verify bottom of wall elevation and if sloped slab elevation from RFI 182 need to be adjusted based on the new details in CCD 49. 2) East interior jacket wall detail 4/S247 clarify if top of sloped slab remains at elevation 91'-0" and bottom of jacket wall at elevation 89'-6" 3) South interior jacket wall detail 1/S241 please clarify if top of sloped slab remains at elevation 91'-0" and bottom of jacket wall at 89'-6" 4) West interior jacket wall typical detail 1/S242 it was discussed that the bottom of the jacket wall be at elevation 86'-0" being that the top of the W12x96 needle beam is at elevation 87'-0" and the 12" interior mat slab bottom elevation is 86"-0". Confirm this is correct assumption. 5) West interior jacket wall detail 5/S249 detail shows a sloped slab. As discussed no sloped slab on west side. Please confirm. 6) West jacket wall detail 2/S242 at the mechanical tunnel the bottom of jacket wall will be at the top of the 24" mat footing. Please clarify this elevation and intent. |  | 1. The top of the sloped slab at the north wall is to be approximately 88’-6”. The top of the needle beams can be adjusted to a higher elevation than 90’ in order to avoid cutting large amounts of stone foundation. This has been discussed with Westland regarding the needle beam elevations. 2. Top of the sloped slab at east wall is to be approximately 88’-6”. 3. Top of the sloped slab at south wall is to be approximately 88’-6” 4. Needle beam locations can be adjusted similar to response #1 above. Bottom of jacket wall will be at elevation 86’-0”. 5. The detail call out 5/S249 is incorrect and should read 3/S249. This change has been issued in CCD 49-R.1 There is no sloped slab on the west side. 6. Please refer to CRSA for FFE of the the 24” mat slab. ¦ We take no exception to that Judd. Thanks ¦ ¦ Based on this direction we will anticipate the bottom of interior jacket walls to be at elevation 87'-0" (18" below sloped slab elevations provided) at south, east and north. At the west the elevation of 86'-0" is noted. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 05/27/2020 |  |  |  |  | Closed | 06/03/2020 | 06/03/2020 | 06/02/2020 | 05/28/2020 | 05/27/2020
494 |  | 0 |  |  | Request for Information | Embed Depth into Addition Mat Slab | I thought the Inspector was going to be good with the email, but it looks like he wants to see Detail 6 on Sheet S210 updated to say 8”. |  | See attached for revised detail. |  |  | High | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 05/27/2020 |  |  |  |  | Closed | 05/30/2020 | 06/02/2020 | 05/28/2020 |  | 05/27/2020
495 |  | 0 |  |  | Request for Information | 3rd Floor Instruction Room, Restroom, and Corridor Ceilings | Per conversation between Mike Yaksick, Pete King Superintendent, David Adams, and Scott Gilberg in the field, please confirm it is acceptable to use 2-1/2" structural studs with 6" structural stud stiff back to strengthen the hard-lid ceilings in the 3rd floor instruction rooms. |  | Please provide spacing of the 2-1/2" studs as well as spacing of the 6" stiff back studs so the structural capacities can be determined. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | Structural Engineers |  | 05/28/2020 |  |  |  |  | Closed | 06/04/2020 | 06/03/2020 | 06/02/2020 | 06/01/2020 | 05/28/2020
496 |  | 0 |  |  | Request for Information | Pipe and Equipment Locations | Please confirm that per conversation between Jason Fullmer and Brian Oswald of VBFA the fountain pumps can be located along the North wall as shown in the clouded area of the attachment. |  | I have forwarded a copy of the RFI to Brian Anderson with Water Design. They are the one's that designed the fountain equipment. I copied you on the email so that you can be part of the conversation. Water Design will need to approve the moving of their designed equipment. |  |  | Medium | Rob Stratton | Stratton & Bratt Landscaping | Brian Oswald | VBFA INC CONSULTING ENGINEERS | 06/16/2020 |  |  |  |  | Closed | 06/04/2020 | 07/20/2020 |  | 06/12/2020 | 05/28/2020
497 |  | 0 |  |  | Request for Information | Cypress Tress around the visitor center | It appears the the cypress tress are suffering from dust mites and spider mites. The arborist got a sample for testing, but we propose that the trees get treated asap. We can preform the work at a T/M rate and get it done tomorrow. The trees have sufficient water but we dont want to see them get past the salvage point. They also have excessive dead needles that need to be cleaned out on the interior of the tree that would take around 4-5 hours to clean up. Please advise on how we should proceed. Thanks |  | This approach sounds reasonable and we would support it. You'll need to submit pricing for review and it will need owner approval prior to starting work. Additionally you'll need to coordinate with the Temple Engineering as they may already have that in their maintenance plans. We do not want to duplicate work if possible. It may also be something they are able to do themselves. Please coordinate with them prior to submitting any costs to the owner for review. Thanks. ¦ ¦ |  |  | Medium | Rob Stratton | Stratton & Bratt Landscaping | Landscape Architects |  | 05/28/2020 |  |  |  |  | Closed | 06/04/2020 | 06/08/2020 | 06/02/2020 | 06/01/2020 | 05/28/2020
498 |  | 0 | 230000 | M102, GI202 | Request for Information | FSD requirements at level 2 instruction room A-3 | Drawing M102, gridline HF at H2 and H4, there are two (2) 18x7 / 14 x 14 return ducts that appear to exit a 1 hour rated wall that do not show any fire smoke dampers. | Please advise if fire smoke dampers are required at these locations, see attached drawings for clarifications. | See comment from VBFA on 18-Jun-2020 ¦ Please see CCD-067 showing revised FSD locations. ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 06/01/2020 |  |  |  |  | Closed | 07/30/2020 | 08/24/2020 | 08/21/2020 | 06/17/2020 | 06/01/2020
499 |  | 0 | 220000 | P111, P110 | Request for Information | Annex level 1, RR 182 | Drawing P111, Restroom 182 indicates a WC-3 fixture to be installed. This WC-3 is a floor mounted water closet. The concrete walls below in the basement conflict with the waste piping that would serve this fixture. See attached drawings for clarification. | Suggestions: #1- installing a wall mount WC-3 fixture and providing a chase behind fixture for access to waste piping. #2- shift the restroom south wall 4.5" to allow the waste line to shift the same amount and be clear of the basement concrete wall. | See response from VBFA. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 06/01/2020 |  |  |  |  | Closed | 06/08/2020 | 06/10/2020 | 06/09/2020 | 06/09/2020 | 06/01/2020
500 |  | 0 |  |  | Request for Information | Session Clocks | Session clocks require a 4" sq 3" deep back box Room 518 shows this clock at an existing stone wall, can we relocate it to a frame wall? Rooms 317 and 319 also are showing session clocks in stone walls there doesn't appear to be any frame walls they could relocate to so we are asking permission to recess a 3" deep box in the wall of both rooms. (see attachments) |  | Relocate session clock in Room 518 to a frame wall where the clock is conveniently viewable and to where a cable can be run. Session clocks in rooms 317 and 319 are essential, and we have been given permission to cut backboxes for these clocks into the stone wall. JiLu Feng Envision Engineering ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 06/01/2020 |  |  |  |  | Closed | 06/08/2020 | 06/09/2020 | 06/09/2020 | 06/03/2020 | 06/01/2020
501 |  | 0 |  |  | Request for Information | Generator Pad | Please confirm we can extend the existing Generator Pad (Shown in Drawing) to accommodate new Generator? New Generator weighs 5300 LB. Will the existing suspended slab support this added weight? We need to core 2- 4" holes 1- 2.5" hole 1- 2" hole and 3- 1.5" holes (approximate locations given in attachment) Under the Generator. is this going to be acceptable? Please see the attached drawing for what is required at the generator pad. |  | It is okay to install the new generator in the location of the old with the added 2+ feet of 4" thick housekeeping pad. Scan slab to insure rebar is not cut during coring. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 06/01/2020 |  |  |  |  | Closed | 06/08/2020 | 06/03/2020 | 06/02/2020 | 06/01/2020 | 06/01/2020
502 |  | 0 |  |  | Request for Information | Ceiling Layout CCD 19 vs ASI 10 | Please confirm if CCD 19 supersedes ASI 10 in relation to the ceiling layout, and confirm the medallions in the hallways goes away. |  | Yes, CCD-19 does supersede ASI-10. No medallions only decorative light fixtures. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/02/2020 |  |  |  |  | Closed | 06/05/2020 | 06/03/2020 | 06/02/2020 |  | 06/02/2020
503 |  | 0 |  |  | Request for Information | East Center Rooms Beam Locations | As discussed on site between David Adams and Zach Hansen: 1. Please provide the locations for the wide flange beams in the clouded areas as shown on the attached drawings. 2. Please provide the design and layout for the new ceiling that is going to be installed as the 5th floor ceiling. |  | See attached marked up drawing. ¦ We will close this RFI upon receipt of CCD 45-R1 for level 5 ceiling. On the other floors we will proceed as directed. ¦ close. ¦ See upcoming CCD-045 R2. ¦ ¦ ¦ Good to hear, let us know when you are able to get it completed. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/09/2020 |  |  |  |  | Closed | 06/05/2020 | 06/16/2020 | 06/15/2020 | 06/03/2020 | 06/02/2020
504 |  | 0 |  | S244 Detail 4 | Request for Information | Epoxy for Detail 4/S244 | On Friday when David Adams, David Rockwell and Zack and where told to use the Hilti RE 500 because that is what was used in the pull test. It has since come to our attention that the RE 500 is to thin to be used with the tubes or socks that normally would keep the epoxy in place. Something to consider is that the pull tests where done using 8” holes (not a very likely to find voids) and we have 16” embedment in some locations (Likely to find Voids). The Hilti rep has said the RE 500 will not work in the screen tubes because it will run out of the tube. Please advise if the 270 was tested or that you want us to use the RE 500 without the screen tubes as designed. In our experience with this project there are voids in the walls and the screen tubes should be used with the 270. This would be a General detail for all anchors in stone walls from here on out. |  | Our understanding is that HY 270 is an acrylic type of adhesive. In previous testing it was discovered that the acrylic based adhesives did not create an adequate bond with the sand stone and pulled out of the wall at very low load magnitudes. Based on this, HY 270 is not approved for this application. Simpson SET XP epoxy is also an approved adhesive for this application. Our understanding is that this epoxy can be used with screen tubes we recommend considering using this epoxy if screen tubes can be used. If it is still desired to use Hilti RE 500 V3 and if voids are being discovered in the wall making it difficult to get epoxy in the holes, then please contact the Hilti representative and see if they have any recommendations on materials that could be placed in the hole to prevent the epoxy from spreading through the voids. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/02/2020 |  |  |  |  | Closed | 06/09/2020 | 06/02/2020 | 06/02/2020 |  | 06/02/2020
505 |  | 0 |  |  | Request for Information | Level 4 Base Replacement | Please advise if the sections of base shown in the attached picture are to be filled in, or if the base in the general assembly room needs to be replaced throughout. |  | These sections are to be filled in. See upcoming CCD-058 for extend of patch and repair. ¦ We will be replacing damaged sections from Mitered corner to Mitered corner where baseboard was cut out for the old heaters. Kyle is currently working on a Revision to CCD 058 (future release) that will show the extent of the work. See attached redline for design intent. ¦ CCD- 058 does not address this question. Please advise? |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/16/2020 |  |  |  |  | Closed | 06/09/2020 | 07/14/2020 | 06/16/2020 |  | 06/02/2020
506 |  | 0 |  |  | Request for Information | Joist Support at Stairs to Tower | When preparing for the removal of the winding stairs accessing the tower. Please confirm that per an onsite conversation between David Adams and Brent White that it is acceptable to install an LVL 2X12 to carry the joists that have been ran short for the stairs. For reference I have included a photo of the current condition. |  | Use an LVL 1.75"x11.875". Attach end of LVL to minimum (3) full length floor joists with Simpson H6 anchors, (1) at each of (3) floor joists. Attach end of LVL temporary support member to stone wall similar to detail 4/S244. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/02/2020 |  |  |  |  | Closed | 06/09/2020 | 06/03/2020 | 06/03/2020 |  | 06/02/2020
507 |  | 0 |  |  | Request for Information | Infill West Side on HF.2 | Please advise if the concrete headers and transitions need to be removed and poured back as shown in detail 10 on sheet S240. For reference I have attached a photo of the current condition. |  | Refer to elevation A/S303. ¦ If the existing headers need to be cut or modified to create room for new openings, then they can must be removed. Otherwise, they can remain in the wall and infilled around as necessary. ¦ Sheet S303 doesn’t address the concrete headers from past remodels. This RFI is resulting from a request from Zach given to Dion that we are to remove all the concrete headers. In the attachment I have clouded the existing concrete that is in question. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/02/2020 |  |  |  |  | Closed | 06/09/2020 | 06/08/2020 | 06/04/2020 |  | 06/02/2020
508 |  | 0 |  |  | Request for Information | Anchoring Audience Seating | Please see the attached photo showing the separations between the planks making up the second level of wood flooring. This has come up as a concern due to the lag screw attachment of the audience seating to the floor. Please advise if additional backing is needed under the floor for the audience seating to anchor to. |  | Provide 2x flat blocking where needed to provide solid attachment of lag screws. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/02/2020 |  |  |  |  | Closed | 06/09/2020 | 06/03/2020 | 06/03/2020 |  | 06/02/2020
509 |  | 0 |  |  | Request for Information | Center Room East-side I-beam Install | In the center room on the east side of the temple it shows the new I beam being installed just after the bottom stair. Please advise if this is the case or if we should move it back to the shirt of the stairs. If it is moved back the joint in the flooring would be hidden under the base board for the shirt whereas if we install it as shown there will be a joint in the flooring tying the new to the old. |  | Move beam under the stairs. ¦ See response from ARW. Move beam under wall of stair platform so the new wood floor runs continuous and to cover joint(s). Provide additional backing at edges as needed to support the new wood floor planks. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/09/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020
510 |  | 0 |  |  | Request for Information | conduit and Floor boxes recessed in pan deck concert slab | Can we recess conduit and floor boxes in pan deck slab as long as we follow and adhere to paramiters of Spec. Division 26 part 3 .3 O (see attachment from spec.) |  | Conduit may not be placed in the slab. Conduit must run above or below the slab on metal deck. Conduit may penetrate thru the slab but shall be spaced at 3D or 4" Min, whichever governs. Floor boxes must be placed above or below the slab on metal deck. If an individual floor box must be placed within the slab, that floor box location must be verified by the Structural Engineer on an individual basis. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/10/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020
511 |  | 0 |  |  | Request for Information | Chandelier supports at LVL'S | Attached is a detail of how we propose supporting chandelier from LVL. If lvl is to close to existing joist we will bridge the gap with a block of lumber and install thru bolt thru joist, block and LVL with unistrut "L" on either side with allthreed hanging the box below as shown in detail. (see attachment) |  | The force that the connections have to be able to support is an arresting force of 2500 lbs. See sketch for required LVL to clip connection. Clips and rods are to be provided by others and are required to be able to support the 2500 lbs arresting force. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/10/2020 | 06/09/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020
512 |  | 0 | 260533 | EP101 | Request for Information | Poke-Thru's and Floor Boxes | On the main level of the annex most of the poke-thru devices will need to be changed to floor boxes because there is no access underneath. these include: Matron Office 120 (1) P1 poke-thru to a B1 floor box Waiting 115 (2) P1-L poke-thru's to B1-L floor boxes Youth 176 (1) P1 poke-thru to a B1 floor box Waiting 109 (4) P1-L poke-thru's to B1-L floor boxes Please advise if this is ok. Also, that leaves only two rooms with poke-thru's: Office 117 and Interview 104. Should we change these to be floor boxes to match the others or keep them as poke-thru's? |  | If areas where poke-thru is called for have no access from below, change to floor box that will match the device requirements specified. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/10/2020 | 06/09/2020 | 06/04/2020 | 06/03/2020 | 06/03/2020
513 |  | 0 |  |  | Request for Information | Historic column dowel embedment detail 1/S248 | See 1/S248. 1) Please provide the embedment depth of the #3 rebar dowel epoxied into column 2) Detail 6/S240 was superceded in CCD 49 with the new column wrap detail on sheet S248. On 6/S240 there was only 1 row of #3 dowels at the top of the column wrap but on detail 1/S248 it shows 2 additional rows. In our submittal 03 3200. 05.01 we asked the question if only 2 dowels were needed each face. It was marked by engineer as ok. Please confirm this is acceptable so we can have documented for the special inspector. |  | 1) Detail 1/S248 shows a horizontal dowel leg length of 16" so in order to fit in the concrete collar wall provide 12" embedment into the stone column. 2) Please use the dowel reinforcing as shown in the shop drawings with 2 dowels on each face. ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/06/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020 | 06/03/2020
514 |  | 0 |  |  | Request for Information | 5th Floor Chandelier Supports | Please advise as to the reinforcement that is to be installed for the Chandeliers on the North and South side of the 5th floor in the historical building. |  | Based on information we received, the lights in these rooms weigh 30lbs. These lights can be supported from the existing roof purlins. If the existing purlins are not in the correct location for support, the light support can be attached to a double 2x6 block that spans between two purlins and is attached to the purlins with face mount hangers with a min. capacity of 250lbs. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/03/2020 |  |  |  |  | Closed | 06/07/2020 | 07/09/2020 | 07/09/2020 |  | 06/03/2020
515 |  | 0 |  |  | Request for Information | Non-Square Rooms Level 5 | Please confirm that the level 5 rooms are known to be out of square per the attached email. |  | It is understood that these rooms are not square. The intent is to leave the historic walls as-is and not attempt to square up the rooms. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/04/2020 |  |  |  |  | Closed | 06/10/2020 | 06/09/2020 | 06/09/2020 |  | 06/04/2020
516 |  | 0 |  |  | Request for Information | Communication conduit from Main MDF to Visitor Center | The conduit route shown on ES101 goes thru the protected tree root systems, Is there an alternate route we should use and if so would pull boxes need to be added? Please advise (see attachment) |  | Is this something you can reroute then change it on the as-builts, or is there a note saying the lines have to be installed exactly as shown on the plans? ¦ Alternate routing of conduits on site is allowed. Additional pull boxes may be required depending on routing. Route on site as needed to avoid issues. Keep path as straight as possible. 270 degree of bends between pull boxes maximum. ¦ Proposed alternate routing is acceptable. Keep total number of bends between pull points to a minimum. No more than 270 degrees total. ¦ ¦ Attached is our proposed route for communication conduits between MDF and the visitor center, it will require only one J box near the visitor center greatly reducing the risk of water flooding into the Annex basement thru conduit. Please confirm this routing is acceptable, if not provide an alternate route showing the locations of the Junction Boxes. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 07/08/2020 | 06/25/2020 | 06/08/2020 | 06/05/2020
517 |  | 0 |  |  | Request for Information | Wood Stairs | E4/AE510 calls for cove mold at stair tread to be paint grade. D2/AE510 calls for the same cove mold to be stained hardwood trim. Which is correct? Typically the cove mold is the same material as the tread. |  | The Cove mold is to be stained the same color as the tread. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 06/09/2020 | 06/08/2020 | 06/08/2020 | 06/05/2020
518 |  | 0 |  |  | Request for Information | Wood Stairs | What is the wood finish of the stair tread? Is this to match the same species as the handrail, African Mahogany or is it to match the flooring in the building? If it is to match the flooring what is the flooring material to be and finish. |  | The wood species is still to be determined by the client. This will be added to a future ASI. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 07/14/2020 | 06/09/2020 | 06/08/2020 | 06/05/2020
519 |  | 0 |  |  | Request for Information | Wood Stairs Sample | Provide a finish sample for the handrail so we can submit a sample. Provide a finish sample of the wood treads if it is different than the handrail. |  | We are waiting on sample of wood floor. Railing will match the wood floor. ¦ Please provide the finished sample of the wood flooring. This is impacting the shop Drawing for the wood trim which has a concerning amount of lead time tied to it. |  |  | High | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 12/03/2020 |  |  |  |  | Closed | 12/06/2020 | 12/10/2020 | 08/12/2020 | 08/12/2020 | 06/05/2020
520 |  | 0 |  |  | Request for Information | Wood Stairs | This is a RFI to the GC. Clarify if wood stairs intermediate landings sub floor and wood flooring is by the flooring contractor. Currently our bid does not include any flooring or sub floor and this would apply to the intermediate stair landings at wood stairs. |  | you are going to be responsible of the stairs only. The flooring contractor will take on the intermediate landings. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Westland PE’s |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 06/25/2020 | 06/25/2020 |  | 06/05/2020
521 |  | 0 |  |  | Request for Information | Wood Stairs | Building codes requires guard rail to be 42”” minimum from top of guard rail to finish floor. Current window guard rail height scales 34”. Clarify if we are to follow code or set guard rail height as shown in architectural elevations. |  | Due to the historic nature of the building and the plywood panel being added between floors to help with the sound transfer, a 42" high guardrail is not needed. The new railing is intended to maintain a similar height at 34-5/8" to match the historic railing that was removed. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 07/13/2020 | 07/10/2020 | 06/08/2020 | 06/05/2020
522 |  | 0 | 230000 | M604, M100 | Request for Information | VAV sizing concerns | Drawing M100, VAV labeled V-0-11 indicates a total of 985 CFMs between all associated supply registers. Drawing M604 indicates a 6" box with 410 CFM max. It would appear this box needs to be a 12" in size to accommodate the CFM requirement. VAV labeled V-0-19 indicates a total of 380 CFMs between all associated supply registers. Drawing M604 indicates a 6" box. It would appear that this box should be an 8" to accommodate the CFM requirement. | Please advise if the VAV box sizes are correct. See attached marked up drawings for clarification. | See response from VBFA. ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 06/18/2020 | 06/17/2020 | 06/17/2020 | 06/05/2020
523 |  | 0 |  |  | Request for Information | Wood Stairs | Detail D2/AE510 and Detail A6/AE510. Current building code calls for 4” diameter sphere shall not pass between balusters, meaning the opening must be smaller than 4”, 3- 15/16”will work. Currently detail D2/AE510 shows 4- 3/8” sphere above the handrail and the true dimension of the space between balusters above the handrail is 4-3/4” on a 12” tread. Detail A6/AE510 shows a 4” sphere passing between the balusters and passing thru the guard rail and the top of handrail. This is not how I understand the code. My understanding is if at any time the 4” portion of the sphere pass thru the balusters the stair does not meet code. Stair treads depths vary depending on the physical field conditions of the job site and depth and rise of a stair also have strict guidelines. Current design of most stair treads for this project is 12” If at any time a tread is greater than 12” the 4” sphere will pass thru the lower portion of the balusters below the hand rail. I have always seen 3 balusters per tread when building a wood stair case on a commercial level. This solves the code issue of space between balusters. Please clarify the understanding of the code and will 2 balusters be acceptable | add 3 balusters per tread | per our review of the code and the attached drawing, we believe our design to be compliant. 3 balusters per tread will add substantial cost and be detrimental to the design. if we feel we are too close to non-compliance, the next best option is to add 1/16" in diameter to each of the balusters. that will close each gap by 1/8". with that said we prefer to keep everything in the design 'as is' until we are certain a change is needed. perhaps a small mock-up of 2 or 3 treads with balusters is the best way to review this. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 07/08/2020 | 07/07/2020 | 06/08/2020 | 06/05/2020
524 |  | 0 | 230000 | M100B, GI200B | Request for Information | Missing FSD's at Level 0.5 | Drawing M100B, GI200B attached, appears there exists 1 hour rated shafts that have sheetmetal duct routing through the shafts with no shown Fire Smoke Dampers. | Please review the attached drawings and advise if FSDs are required in these locations. | See response from VBFA dated 30-June-2020 ¦ Please see comments from VBFA and refer to CCD-069 reflecting the revised Baptistry restroom layouts. ¦ The mechanical plan referenced is outdated. Please refer to CCD-067 and CCD 069 for the revised layouts. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 09/29/2020 |  |  |  |  | Closed | 07/30/2020 | 10/08/2020 | 10/02/2020 | 06/08/2020 | 06/05/2020
525 |  | 0 |  |  | Request for Information | CCD 35's Impacts on Ceilings | Hall 044 in the Annex was extended in CCD 35 but the ceiling and lighting layouts were not updated. | Provide direction on how you would like these laid out. | This was also recently noticed by CRSA and has been updated. It will be released along with other basement changes in CCD 054. Extend the Ceiling, Crown, and add a 3rd decorative fixture. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/05/2020 |  |  |  |  | Closed | 06/12/2020 | 06/25/2020 | 06/09/2020 |  | 06/05/2020
526 |  | 0 |  | C.5 / LL100 / LL510 / LL511 / LL512 / LL513 | Request for Information | 400 South Site Fence | Per Sheet C.5 – Demo Plan Temple Block (attached), Note D07 directs contractor to “Refer to Landscape Plans for removal and relocation of fence”. Referring to the Landscape Drawings notated above, there are new site fencing details however, there is no direction on the extent of the fence demo scope – specifically the removal of existing metal fencing, precast panels, gates, and step footings. Please confirm that the existing metal fencing, precast panels, gates, and footings are to be demolished and disposed of. Please provide direction regarding the extent of this demo/replacement; i.e. is it the complete fence from corner of 200 East to corner of 300 East? The current C.5 plan illustrates just (1) PRCAST PANEL HIGHLIGHTED WITH Note D07, Should this be typical for all precast site wall panels on 400 South? Should the Demo include the metal fencing and gates as well? Costs are anticipated with this work. Please advise. |  | See layout sheets LL101 and LL102 for callouts identifying which fence panels and precast panels are to remain and where new sections are to be provided. This is also shown in the fence elevations on LL512. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 09/22/2020 |  |  |  |  | Closed | 06/15/2020 | 11/19/2020 | 06/25/2020 |  | 06/08/2020
528 |  | 0 |  | C.5 / LL100 | Request for Information | 500 South and 200 East Site Fence/Gates | Per Sheet C.5 – Demo Plan Temple Block (attached), Note D07 directs contractor to “Refer to Landscape Plans for removal and relocation of fence”. Sheet LL100 (attached) appears to show intent for work associated with the existing fence/gate but has no callouts or direction. Is it intended to demo and replace these fence/gates? If demolition is anticipated, to what extent…metal fencing, step footing, etc? Please clarify put-back requirements as well. Costs are anticipated with this work. Please advise. |  | Refer to discussion in the field on June 16th. Remove fence panels and any associated angles, plates, and hinges. Fill void area with new fence panel, provide seemless transition from existing fence to remain and new infill panel. Provide curb below fence, anchored to existing curb on either side of infill area. |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 10/08/2020 |  |  |  |  | Closed | 10/11/2020 | 10/29/2020 | 06/25/2020 |  | 06/08/2020
529 |  | 0 |  |  | Request for Information | Embed and Through Bolt Clash | Please confirm it is acceptable to move the top two through bolts to 6" from the edge of the column? Per a conversation between Carter Cluff and Zach Hansen The reason for this request is due to the Nelson studs being exactly where the through bolts land. |  | Confirmed |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/08/2020 |  |  |  |  | Closed | 06/11/2020 | 06/08/2020 | 06/08/2020 |  | 06/08/2020
530 |  | 0 |  |  | Request for Information | Chandlers Center Lever 4 | Please confirm that the direction given from Scott to David and Jason on site (See attachment) is how we are to proceed with locating the chandeliers on the level 4 ceiling for the north and south wings. |  | Confirmed, The intent is to center the Medallion / Chandelier on the flat portion of the ceiling (between edge of crown and edge of Entablature/Capital) |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/08/2020 |  |  |  |  | Closed | 06/11/2020 | 06/09/2020 | 06/09/2020 |  | 06/08/2020
531 |  | 0 |  |  | Request for Information | Roof Trusses New Construction vs Existing | It appears that in the model there are two different colors the gray designating existing and the light brown are the wood member that I can only assume need to be removed and replaced with new wood members. Please advise |  | The two different colors are likely due to them being from the structural models and mechanical models. No truss members are to be removed and replaced. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/08/2020 |  |  |  |  | Closed | 06/15/2020 | 06/08/2020 | 06/08/2020 |  | 06/08/2020
532 |  | 0 | 230000 | M100B | Request for Information | Concrete encased duct | Drawing M100B, level 0.5 is now indicating sheetmetal ductwork to be installed within concrete encasement. No specifications appear to call out for sheet metal duct installation means and methods within concrete encasement. Please provide sheetmetal specifications for installation within concrete encasement. | See attached drawing with clouded area. Would recommend the use of G90 galvanized sheet metal duct for install at these locations within the concrete at no additional cost. If a vinyl chloride coated steel is required for sheet metal fabrication and install, additional cost would apply. | See comment from VBFA ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 06/08/2020 |  |  |  |  | Closed | 06/15/2020 | 06/11/2020 | 06/10/2020 | 06/08/2020 | 06/08/2020
533 |  | 0 |  |  | Request for Information | Joist Removed for HSS Level 2 | Please confirm that at the rim board around the 2nd floor domed ceiling we are to remove the floor joist and flooring material above in preparation for the Ducting Chase, HSS Post’s and LVL walls. For reference I have attached some drawings and pictures to illustrate condition in question. |  | Yes. This is the intent of the design. ¦ See ARW's response |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/08/2020 |  |  |  |  | Closed | 06/15/2020 | 06/16/2020 | 06/11/2020 |  | 06/08/2020
534 |  | 0 | 230000 | AE4303 | Request for Information | Room 309-Low wall HVAC return | Drawing AE4303, room 309, drawing does not call out any dimensions or indicate any key notes addressing low wall duct return register locations. See attached dimensions for what has been modeled and installed to date. Please advise that the ductwork at these locations has been installed. | Please confirm the attached drawing with mark up dimensions for locations of return wall registers is correct. | the attached drawing titled "RFI Response level 3" came from a meeting with Jason, Scott, David, Dion and Craig. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 06/08/2020 |  |  |  |  | Closed | 06/15/2020 | 06/09/2020 | 06/09/2020 | 06/09/2020 | 06/08/2020
535 |  | 0 |  |  | Request for Information | Duct and Ceiling Elevation Conflict at Electrical Room 315 | Reference AE123 and attached screen shot from the BIM model. From finish floor to bottom of duct in electrical room 315 is 8’-9 5/16”. The finished ceiling elevation is 9’ -2 ½” per AE123. Should the ceiling be lowered and if so to what elevation? |  | Install a soffit drop around the lowered duct. See ASI012. Note that the duct has been moved 12" north away from the door transom. |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 06/09/2020 |  |  |  |  | Closed | 06/15/2020 | 07/08/2020 | 07/02/2020 |  | 06/09/2020
536 |  | 0 |  |  | Request for Information | 7-8” of Gravel Under Historical Mat Slab | Please confirm we are to install 7-8” of gravel under the mat slab in the Historical building. |  | Yes, please provide 7-8" of gravel base. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/09/2020 |  |  |  |  | Closed | 06/16/2020 | 06/09/2020 | 06/09/2020 |  | 06/09/2020
537 |  | 0 |  |  | Request for Information | Attic Catwalk East End | Please see the attached drawing and advise if we can make the adjustment. This question/adjustment was discovered when comparing the catwalk layout with the mechanical layout. It was discovered that the embeds for the LVL’s where in line with the HVAC duct penetrations passing through the stone wall. Hopefully this will be the last question on these catwalks |  | This framing is acceptable structurally. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/09/2020 |  |  |  |  | Closed | 06/16/2020 | 06/11/2020 | 06/10/2020 | 06/10/2020 | 06/09/2020
538 |  | 0 |  |  | Request for Information | HSS Under Wide Flange Gridline HC | In the second-floor steel assembly is it acceptable to install an the HSS on the corner of the column jacket for the single I-Beam running along the HC gridline I have attached an excerpt from the drawings for reference. The attached sketch is given as a possible option. |  | Adding a column at the proposed location appears to conflict with the architectural layout of the rooms in this area and would result in the column being in the floor space. What is the reason of the beam being at the corner of the column rather than on the Grid Line HC as shown in the drawings. It was anticipated that this new steel beam would attach to the center of the column and be connected to the new column steel collars per the answer to RFI 460. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/10/2020 |  |  |  |  | Closed | 06/12/2020 | 06/11/2020 | 06/10/2020 |  | 06/10/2020
539 |  | 0 |  | AE524 | Request for Information | Font Witness Platform Stone Deck | Please provide details of stone thickness and setting bed requirements. For Clarity I (David) have attached a drawing showing the area in question. They have planned on doing a bronze finish in these areas but the review comments call for the Las Vegas sandstone. |  | The stone flooring is 2 cm (3/4") and can be set in Thinset in these locations. |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 06/10/2020 |  |  |  |  | Closed | 06/17/2020 | 06/24/2020 | 06/22/2020 |  | 06/10/2020
540 |  | 0 |  | HACI Shop Drawing Sheet 1.2 (Review Note) | Request for Information | Font Witness Desk Electrical Box and Conduits | Please provide the size and type of electrical box required. Also, the size and number of conduits required. | There is a problem with this design being code compliant. An electrical receptacle can't be located within 6' of the edge of the pool, i believe the best solution would be to eliminate the floor box and stub conduit directly to the witness desk and do a hard connection rather than cord and plug. (this is a grey area) | Electrician will need to provide exact box sizes to be installed. Per design, a GFCI protected receptacle and data outlet is required at the font desk for the font system recorder equipment . The hard wired proposed option will be a challenge as the desk and equipment is cord and plug and typically designed to be able to be moved if necessary. Can the outlet box be moved further from the opening of the font so that it can be a cord length of 6ft away from waters edge ? If not possible, can an exception be requested from local inspector due to unique circumstances of the installation and that the outlet is only used for connecting the permanent font desk system, this is not a pool/spa as the code is intended for? ¦ The floor box dimensions are 5"X8" we will also need a chase large enough for 2-1" conduits from the floor box one of the legs the dimensions for the floor box location are attached to RFI 361 like the electrical engineer said in his response if there is room to move box so something plunged in with a 6' cord could not go into the water we should do this. ¦ Jason/Trask, Is this something you can help me with. ¦ ¦ ¦ Can I get your input on this? |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | Trask Johnson | Wilkinson Electric Inc | 06/10/2020 |  |  |  |  | Closed | 06/17/2020 | 08/12/2020 | 07/28/2020 | 07/09/2020 | 06/10/2020
541 |  | 0 |  |  | Request for Information | 5th floor lighting in sealing rooms | Due to multiple building restraints IE. duct work, framing, j boxes mech. and sprinkler piping. We are asking for an exception to use MC cable to supply the lighting in the 5th floor proxy sealing rooms 5-17, we will pipe the switches in each room together with .75 EMT Conduit and run the switch legs in each room to recessed cans in that room with MC cable. This will also allow for future height and side to side adjustment of the recessed cans if there is a flexible connection to them. |  | This is acceptable in this location. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 06/10/2020 |  |  |  |  | Closed | 06/17/2020 | 06/16/2020 | 06/11/2020 | 06/11/2020 | 06/10/2020
542 |  | 0 |  |  | Request for Information | Patron Housing Communication J Box | ES 101 shows us connecting a 4" conduit into an existing J Box at Patron Housing. Could this J Box be Located for us? (see attachment) |  | Per phone discussions with Brian and Kory, the in-grade communication pull boxes that were to be installed as part of the previous patron housing electrical and comm utility upgrades projects were not installed per plans and do not exist at the breasway between the housing units as thought. It is recommended that the conduits shown in the temple site plan be routed as close to the existing patron housing existing communication boxes as possible in order to simplify possible future connections of fiber from temple/visitors Center to family search to the south. Provide pull string, cap and label conduits for future locating. Adjust routing around trees/root balls as necessary, but minimize number of bends. Brian and/or Kory indicated they would reach out to Owner's ICS group to confirm their latest direction on fiber connections (currently outside of contractors scope of work). ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 06/11/2020 |  |  |  |  | Closed | 07/05/2020 | 07/08/2020 | 06/25/2020 | 06/15/2020 | 06/11/2020
543 |  | 0 |  |  | Request for Information | Annex north mat footing epoxy dowels | At existing mat footing north side between grids AF and AD and A10 on sheet S100 there is a section of the #4 epoxy dowels that will not be able to be installed with only a 3'-3" gap with the forms and waterproofing in place. with the current requirement of 24" embedment and 36" development per detail 13/S210. Per discussion with Zach by phone and reviewing onsite with Matt on 6/11 confirm acceptable to bend bend the bottom dowel as marked up on attachment |  | Yes. This is acceptable. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 06/11/2020 |  |  |  |  | Closed | 06/18/2020 | 06/17/2020 | 06/17/2020 | 06/15/2020 | 06/11/2020
544 |  | 0 |  | CCD-044R1, EL601 | Request for Information | Elevator Cab Lights | CCD-044R1 added fixture types DR5A and DR5A-E to the light fixture schedule, EL601. These fixture types are for the elevator cabs but are not shown on the plans. How many of each type go in each elevator cab? |  | Elevator cab lighting layouts were added as part of CCD-057. ¦ ¦ Thanks for the heads up. I'm going to leave it open until we receive the CCD-057 |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 06/12/2020 |  |  |  |  | Closed | 06/19/2020 | 07/13/2020 | 06/25/2020 | 06/15/2020 | 06/12/2020
545 |  | 0 |  |  | Request for Information | Structural Coordination West Wall Penetrations | There are two types of questions on the attached pdf: Some of the questions have to do with the design showing part of the West wall being notched out to allow for duct work to be run into the projector room but there isn't any structural reinforcing shown. The others are regarding pipe penetrations that need to be made in the structural reinforcing for a duct penetration. | Please advise how you would like us to handle these two types of situations structurally. | After discussion with Jason Fullmer while on site, we determined the following: 1- It was determined that the large notch shown in the model is not required. The duct work serving the projector box is small enough to fit inside the metal stud walls without needing to notch the stone wall. 2- The piping is to be moved down directly above the duct work and then the new penetration can be made large enough that the piping and duct work will fit in a single large opening. The opening can then be constructed per directions given in RFI #316. ¦ |  |  | High | Jason Fullmer | Westland Construction, Inc. | Westland PE’s |  | 06/12/2020 |  |  |  |  | Closed | 06/15/2020 | 06/25/2020 | 06/18/2020 | 06/25/2020 | 06/12/2020
546 |  | 0 |  |  | Request for Information | Area Well Depth - South Side Historic Building | Please confirm that per the attached drawing we are to install in the South area wells a 4” concrete slab, at 6” under the HVAC exhaust line. For reference I have attached some documents applicable to this question. |  | See comment from VBFA |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 06/15/2020 |  |  |  |  | Closed | 06/22/2020 | 06/18/2020 | 06/17/2020 |  | 06/15/2020
547 |  | 0 |  | C.11 / C.11.1 & Remain Civil Drawings | Request for Information | Civil Drawing Discrepancies - Sheet C.11 on CCD_59 | Over the course of the project there have been various different versions of the same sheet number. For example: The version of C.11 on CCD_59 is titled UTILITY - WATER - 300 EAST STREET which is a completely new and different page compared to the version of C.11 provided in the conformed set which is titled PLAN & PROFILE - 400 SOUTH STREET. This drawing is also different I'm assuming from the one in the Civil section of Drawing Index Gl002.1 which shows a C.11.1 - PLAN - 300 EAST STREE but that drawing wasn't included in the conformed set. I know C.1 through C.7 all also have duplicate drawings floating around (the normal set and a set for offsite utilities). | Re-issue a complete set of civil drawings using unique drawing numbers. | I have uploaded the latest plans. |  |  | High | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 06/15/2020 |  |  |  |  | Closed | 06/19/2020 | 07/23/2020 | 07/02/2020 |  | 06/15/2020
548 |  | 0 | 211000 |  | Request for Information | FDC Location on South Fire Lane | Per Sheet PS100 note #23 “Free standing remote FDC, coordinate with landscaping for exact location. Piping to be sloped toward the building…” Referring to the landscape drawings, there is no direction given for the piping installation, FDC location, FDC type, or material type. In spec 21 1000-21: 2.18 B, there is information for a wall mounted but no mention for free standing. Also, FP501 detail 5 note 6 states “free standing FDC coordinate exact location civil.” This location is not found in the civil drawings. Please provide direction for FDC location and piping elevation location for needed slope? FDC free standing detail and piping material? Related Documents: PS100 – note 23: FDC coordinate with landscaping for exact location…See FP100 FP100 – note 6: to remote FDC see sheet PS100 for continuation and 10: Lateral fire main into building. See civil for continuation. FP501 – Spec 5 note 6: “free standing FDC coordinate exact location civil.” |  | See the attached sheets for FDC location. We will want to use Croker 65332 Four-Way Square Freestanding Inlet FDC Model 6532 for the FDC. ¦ Do you guys know anything about this? Can you help me resolve this? I wasn't aware of an FDC line. Where does this leave the building and where is it supposed to go? |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 08/20/2020 |  |  |  |  | Closed | 06/23/2020 | 09/22/2020 | 08/26/2020 | 06/19/2020 | 06/16/2020
549 |  | 0 |  |  | Request for Information | Top of Steel Elevation | The steel members south of A1 and north of H5 (see attached) are not located as far as elevation. Please provide a top of steel elevation for these members. |  | Top of Steel is 113' - 2" across this hallway south of Grid A1 to Historic North Wall ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 06/16/2020 |  |  |  |  | Closed | 06/23/2020 | 07/23/2020 | 07/21/2020 | 06/17/2020 | 06/16/2020
550 |  | 0 |  |  | Request for Information | Blindside Waterproofing between Hist. and Annex. | Please confirm that per a site conversation the area in Yellow does not need to have the blindside water proofing installed under it. |  | This is correct, verify vapor barrier is used in place of water proofing |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/16/2020 |  |  |  |  | Closed | 06/23/2020 | 07/08/2020 | 07/07/2020 |  | 06/16/2020
551 |  | 0 |  | LI101 | Request for Information | Visitor Center Existing Main Irrigation Line | Question: Per Sheet LI101 – Irrigations Overview (attached), the clouded area around the visitors center shows “Existing 4” Main Line” that is intended to stay. We performed a pressure test on the existing 4” main line and lost 48 lbs. of pressure in less than 1 hour. Considering the pressure test results and the pictures showing the condition of the existing material, there is some concern leaving the “Existing 4” Main Line”. Please advise. |  | MGB+A RESPONSE: Based on the information provided from the contractor in the RFI-551 we recommend providing new 4" mainline of the same type as the current new 4" mainline that has been installed. The Landscape contractor is to provide additional information on cost to replace the existing mainline in question. Costs to be reviewed and approved prior to proceeding. MGB+A: Brandon Ruiz 7-7-2020 ¦ This was responded to July 7, 2020. It is still showing up as 'outstanding'. ¦ ¦ ¦ July 31 there was a PDF attached about a different route for the 4" irr. main line. Stratton and Bratt are putting costs together for this second option. Please review this PDF for rerouting the main line. This route would be less costly and would not impact the site outside of the fence. |  |  | High | Zac Givens | Westland Construction, Inc. | Brandon Ruiz | MGB+A The Grassli Group | 07/31/2020 |  |  |  |  | Closed | 08/03/2020 | 08/20/2020 | 08/11/2020 | 07/09/2020 | 06/16/2020
552 |  | 0 |  |  | Request for Information | Door Dimensions Grid A1 | We can't find any center of door dimensions for the doors along grid A1. |  | Dimensions were provided on sheet AE147 (Delta 53) in response to RFI 472. Please advise if additional information is needed for these openings. |  |  | High | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 06/17/2020 |  |  |  |  | Closed | 06/20/2020 | 06/24/2020 | 06/22/2020 |  | 06/17/2020
553 |  | 0 |  |  | Request for Information | North Addition - Cored Hole Locations | Per the structural notes we need approval before we core drill. We are planning on coring these locations along grid A2 at the fire riser room location in the SW corner of the North Addition. Please see the attached locations. |  | The proposed locations are acceptable. |  |  | High | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 06/17/2020 |  |  |  |  | Closed | 06/20/2020 | 06/23/2020 | 06/18/2020 |  | 06/17/2020
554 |  | 0 |  |  | Request for Information | Door Types drw AE611 | Door type 24 is not clarified in the door schedule if this doors is wood or metal Please clarify. Original door schedule at bid time said door was to remain but never called out if this was metal or wood. Door type 24 is door # 34, a pair of doors with louvers to the Mechanical Room. |  | This will be a hollow metal door and frame ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/18/2020 |  |  |  |  | Closed | 06/25/2020 | 07/23/2020 | 07/21/2020 | 06/23/2020 | 06/18/2020
555 |  | 0 |  | AE610 | Request for Information | Door 101A and 101B door thickness | Door 101A and 101B are door type 15. Door type 15 detail AE610 refers to door section B3/AE610 which calls for insulated glass and door thickness to be 2 1/4". Current door schedule AE601 call for door to be 1-3/4" thick. Clarify door thickness for door 101A and 101B. If door needs insulated glass door will need to be 2-1/4" thick |  | Doors 101A and 101B door type and detail B3/AE630 is correct and will be 2-1/4" thick with insulated glass. Please disregard the 1-3/4" thickness shown in the door schedule. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/18/2020 |  |  |  |  | Closed | 06/25/2020 | 07/23/2020 | 07/21/2020 | 06/23/2020 | 06/18/2020
556 |  | 0 |  |  | Request for Information | Dutch door # 082 type 17 | Door type 17 AE610 calls for height of transaction top to be 36". Hardware schedule calls for and escutcheon "B" which is 9 1/2" . In order for door handle to be at 38" and escutcheon not to be cut in half the transaction top needs to move to 42" height ( stand transaction height). This will allow handle and escutcheon plate to all be on the lower half of the door and door handle will align with other doors handles in the same area. Confirm if transaction height can move to 42" |  | 42" high transaction top is acceptable. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/18/2020 |  |  |  |  | Closed | 06/25/2020 | 07/23/2020 | 07/20/2020 | 06/23/2020 | 06/18/2020
557 |  | 0 |  |  | Request for Information | Door handle height | Not all door handle heights are called out on door types drw AE610. Some types show handles to be lower than code such as type 14, 19, 2, 4, Clarify door handle heights on all door types. |  | As a general Rule, the hardware is to be centered on the lock rail. For the majority of the doors this will be at 3'-2". On the round top wood doors this will be at 2'-10". Existing doors will have the new hardware placed in the same location as the old hardware. Dimensions will be provided in CCD 101 Type 2 = 3'-2" Type 4 = 2'-10" Type 14 = 3'-2" Type 19 = 3'-2" ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 06/18/2020 |  |  |  |  | Closed | 06/25/2020 | 12/17/2020 | 12/10/2020 | 06/23/2020 | 06/18/2020
558 |  | 0 | 230000 | See attached | Request for Information | HVAC finish opening locations | Various HVAC finish registers and grilles are shown on the architectural drawings that do not appear to have any center line dimensions or locations required shown. See attached drawings indicating finish HVAC grilles with no dimensions or measured locations. | Please indicate locations of finish HVAC registers per grid lines on the attached architectural drawings to allow installation in the correct locations. | Please refer to forthcoming ASI from CRSA locating all grilles. ¦ Please refer to attached ASI #32, thanks. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/07/2020 |  |  |  |  | Closed | 06/29/2020 | 07/13/2020 | 07/08/2020 | 07/07/2020 | 06/22/2020
559 |  | 0 |  |  | Request for Information | Hist. Basement Column Jackets | Please confirm that: 1. Attached drawings are for the columns on the HC and HE grid lines. 2. The second sheet is regarding the bump outs for Baptistery Font along grid-line H3 |  | Things discussed in the 6/22 phone call with Dave at Westland: How to attach concrete columns CC-3 and CC-6 on grid H3, sheet S100A to the mat slab below. See detail 10/S210 as this is a similar condition. There was discussion that the CC-6 48” wide columns on grid H3, sheet S100A would not be large enough to be able to support the W14x30 beams. Based on our drawings these columns should be large enough if centered on the two W14x30. Please notified ARW if this is not the case. The existing columns are slightly off position from where they were originally thought to be. Also, sand blasting has made them slightly smaller than originally. Because of these and other factors, the jacket wall on several of the existing columns needs to be widened by approximately 6” to allow the W14x30 to attach. Please see attached detail for information on how to accomplish this. It is our intention that the reinforcement being called out be new and that what has been tied previously remain as is. This is for the columns on grids H2/HC, H4/HC, H2/HE, H4/HE. 4. The 16”x16” CC-3 callouts at the ends of the baptismal font oval foundation need to be shown proud of the oval. The question was asked as to how to accomplish the reinforcing with the column being proud. See attached detail. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/23/2020 |  |  |  |  | Closed | 06/26/2020 | 06/23/2020 | 06/23/2020 |  | 06/23/2020
560 |  | 0 |  |  | Request for Information | 4th floor recessed can locations | confirming as per conversation between Jason Fullmer and Scott Gilberg 06/23/2020 we are moving can lights and chandeliers 1" off of center toward outside of building. (see attachment) |  | I have confirmed with Scott the conversation between him and Jason. Moving the recessed lighting 1" from center is acceptable to avoid the existing joists. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 06/23/2020 |  |  |  |  | Closed | 06/30/2020 | 07/15/2020 | 07/14/2020 | 06/23/2020 | 06/23/2020
561 |  | 0 |  |  | Request for Information | Ducts Passing Through Corr. Walls | Please confirm we are to frame out the duct penetrations that were made to existing walls. ie: head off the wall at locations like shown in the attached photo. |  | Confirmed. Please provide 2x headers above and below the penetrations to provide stability to the cut studs. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/23/2020 |  |  |  |  | Closed | 06/26/2020 | 07/08/2020 | 07/06/2020 | 07/06/2020 | 06/23/2020
562 |  | 0 |  |  | Request for Information | New Roof Drain Cleanouts / Stormdrains | Per CCD 59 – C.8 (see attached) . Two Questions: It shows new RDCO #3, 4, and 7 in the fire lane concrete. Please confirm the onsite conversation with the landscape architect that these clean outs can be moved to the planter area closer to the temple. (clouded in purple) Please confirm that SDCO #21, 23, 25, 26, and 27 can be deleted. (clouded in green) |  | Yes, RDCO 3,4, and 7 can be moved out of concrete. There are trees right next to the concrete walkway. As long as the cleanouts are between the proposed trees and the historic temple. Look at the attached image for reference. The blue dots would signify the location that the cleanouts could be placed. ¦ In response to question #2, yes the SDCO's clouded in green can be deleted. ¦ Question 2 was discussed in the field. Please confirm they can be deleted. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 06/23/2020 |  |  |  |  | Closed | 06/30/2020 | 07/23/2020 | 07/10/2020 |  | 06/23/2020
563 |  | 0 | 086300 |  | Request for Information | METAL-FRAMED SKYLIGHTS COLOR SELECTION | Do you want the skylight to match the interior wall white color (OC-13 Soft Chamois) or the interior trim white color (OC-130 Cloud White)? NOTE: The linked submittal for the Metal-Framed Skylights matched the standard skylight colors to the trim white color not to the wall white color. |  | It needs to match our trim, however it is a custom munsell color. We are waiting on paint submittals still for the paint. This is the first time I have heard about 0C-13 Chamois. |  |  | High | Doug Moore | Jones Paint & Glass - St. George | Interior Designer |  | 06/24/2020 |  |  |  |  | Closed | 07/01/2020 | 08/12/2020 | 08/12/2020 |  | 06/24/2020
564 |  | 0 |  |  | Request for Information | Fire alarm tie-in to mag hold opens | There are no 120V circuits assigned, or fire alarm tie-ins for the mag hold opens. These are the doors that will have ABS-supplied hold opens: 052, 068A, 184B, 201A (2 ea), 301A, 401A (2 ea), 501A. Please advise on power and fire alarm for these door holders. | We suggest using 120V circuits from nearest panelboard to power the hold opens, and a fire alarm control module on each floor to control them. | Electrical design was based on 12-24v mag hold opens. If 120v is the only available option we can provide additional 120v circuits. ¦ ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 06/25/2020 |  |  |  |  | Closed | 07/02/2020 | 07/08/2020 | 06/29/2020 | 06/26/2020 | 06/25/2020
565 |  | 0 |  |  | Request for Information | Remove the Level 4 Vestibule Ceilings | Please confirm that per the OAC meeting on June 18th that we are to remove the ceilings of rooms 409 and 411. This would allow us to be able to work out the routing of the electrical and lighting layout of these rooms. |  | Dave, the lath and plaster ceilings are to be removed in these rooms, that is correct. The plaster crown molding in these rooms is to remain and needs to be protected in place. The center medallions also need to remain in place and be protected. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/25/2020 |  |  |  |  | Closed | 07/02/2020 | 07/08/2020 | 07/07/2020 |  | 06/25/2020
566 |  | 0 |  |  | Request for Information | Levels 3 and 5 Existing Door Frames | Please advise if we are to remove the hallway door frames on levels 3 and 5. If so, are we to remove all the plaster on the adjacent walls as well? |  | Dave, It is likely that these frames will come out, but is contingent upon PR #4 being approved. Thanks |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/25/2020 |  |  |  |  | Closed | 06/29/2020 | 07/13/2020 | 07/07/2020 | 07/08/2020 | 06/25/2020
567 |  | 0 |  |  | Request for Information | East Tower Elevation | We have found an elevation differences from the North to the South of center room on the East tower. North side used as base measurement. The South side height changes are differences in relation to the North side. The dimensions provided where done for reference. If conformation is desired, we can make these locations access able to a surveyor. |  | Contractor to split the difference at each room as per conversation with Dave Adams on 7/17/20. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/26/2020 |  |  |  |  | Closed | 06/29/2020 | 07/21/2020 | 07/20/2020 |  | 06/26/2020
568 |  | 0 |  | S302 | Request for Information | Preload 2nd and 4th Floors I-Beams | In order to minimize any dipping of the floor when it is loaded with occupants do we need to plan on pre-loading the I-Beams in the center of the Span. If so please provide how much it will need to be loaded? |  | The beams do not need to be pre-loaded as long as all of the joists are shimmed tightly so that loads will be transferred directly to the beams without any need for the existing truss to deflect before loads are transferred to the new beams. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 06/26/2020 |  |  |  |  | Closed | 07/03/2020 | 07/01/2020 | 06/29/2020 |  | 06/26/2020
569 |  | 0 |  |  | Request for Information | East Center Room Crown Removal | During the owners walk in the ease center room on level 4 it was discussed that the upper part of the Crown Molding attached to the ceiling will be pulled out with the ceiling. The lower part will be removed because it will interfere with the door trim. Please confirm that these are to be removed. If not, please advise. We need a quick response on this because on Monday we have the demolition contractor onsite and we want him to start this area. |  | Dave, per CCD 043, the entire crown molding is to be removed with the ceiling, both the upper and lower portions. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/26/2020 |  |  |  |  | Closed | 06/29/2020 | 07/08/2020 | 07/07/2020 |  | 06/26/2020
570 |  | 0 | 260573 |  | Request for Information | Larger frame breakers with LI trip units per study review | Larger frames with LI trip units for a few breakers and upgrade to I-line for panelboard HE are required to meet coordination recommendations (see attached). How should we submit the additional costs that will be incurred for this? Should we just reference this RFI? |  | will you please provide me the product data for thee larger breaker. ¦ provide breakers/equipment as required to meet selective coordination requirements per one-line diagram notes and specification section. ¦ for reference David Barney has attached the product data for the breakers mentioned in the RFI. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 06/29/2020 |  |  |  |  | Closed | 07/06/2020 | 07/21/2020 | 07/16/2020 | 07/13/2020 | 06/29/2020
571 |  | 0 |  |  | Request for Information | Precast Concrete Unit Paving Response | 1) The corner cap detail was marked up to have a 45 degree miters. This detail leaves a sharp edge exposed to pedestrian traffic and is vulnerable to shipping. By having a return at the corner, the edges are softened and less likely to chip. 2) The paver detail shows two small wedge-shaped pieces at the outside corner. Putting smaller pieces on the outside corner becomes a maintenance problem. The smaller pieces tend to shift and become trip hazards For reference drawings depicting these conditions have been attached |  | See attached response ¦ Reposting the attachment - see comments. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 10/27/2020 |  |  |  |  | Closed | 07/07/2020 | 10/28/2020 | 10/23/2020 | 08/12/2020 | 06/30/2020
572 |  | 0 |  |  | Request for Information | CW4 connection at temple grid AA.5 | See S100 around grid AA.5/A1 At the CW4 wall that butts into the jacket wall and existing temple wall is this wall independent or does it need to dowel into the stone or have corner bars into the exterior north jacket wall? |  | Please provide corner bars into the jacket wall. Corner bars are to match the horizontal reinforcing of the CW-4 wall. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 06/30/2020 |  |  |  |  | Closed | 07/07/2020 | 07/08/2020 | 07/02/2020 | 07/01/2020 | 06/30/2020
573 |  | 0 |  |  | Request for Information | Room 518 Ceiling Elevation | When trying to find the correct ceiling height for room 518 we discovered a discrepancy. Please advise if the 11’-2” as shown on sheet AE125 is correct or if it’s to be 10’-8 ½” that was given to us on May 20th. For reference I have attached Sheet AE125 and the Email provided on the 20th. |  | Please use the 10'-8 1/2" ceiling height for this room. Thanks |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 06/30/2020 |  |  |  |  | Closed | 07/12/2020 | 07/15/2020 | 07/15/2020 |  | 06/30/2020
574 |  | 0 |  |  | Request for Information | Pneumatic Door Operators | The entry doors call for pneumatic closer with tubing and a compressor. In the past we’ve ran into a couple issue; the compressor being too noisy, and when placed too far away to reduce the noise, air pressure is lost by the time it gets to the closer. They struggle opening two doors at the same time and tend to be a maintenance issue for future years. Typical on other temples they‘ve gone with a power auto-operator. This gives more control over the doors and will have less maintenance issues in the future. I would recommend doing something like what was done on Jordan River and Haiti. In the attachment the items in Red are components for the pneumatic closures. |  | After discussion with the owner and contractor, the decision has been made to stay with what is specified in the drawings. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/01/2020 |  |  |  |  | Closed | 07/07/2020 | 08/11/2020 | 08/10/2020 |  | 07/01/2020
575 |  | 0 |  |  | Request for Information | Additional Joist Hangers | Please confirm the install of additional joist hangers as outlined in ARW’s field repot 22 item 4. Joist hangers to be installed on the joist ends that are not bearing at least 1” are to have a new saddle installed on them to assist in carrying the joist load to the truss. The saddle is to be a Simpson HU2.1/9. |  | Confirmed. Please verify with framing subcontractor that the Simpson hanger will work for the existing joist size. Substitutions for a different hanger is acceptable provided it meets a minimum load capacity of 1,500lbs. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 07/01/2020 |  |  |  | 15000.00 | Closed | 07/04/2020 | 07/01/2020 | 07/01/2020 |  | 07/01/2020
576 |  | 0 |  |  | Request for Information | Basement Column Strong Pipe Core | Please advise if we are able to core the two 9” holes into the columns in the basement for the Strong pipe or if we need to do one at a time. |  | Please core (1) hole and then install the pipe through the hole before the next hole is drilled. It is not necessary to grout the pipes solid at this point, just place the pipes in the newly cored hole. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 07/01/2020 |  |  |  |  | Closed | 07/04/2020 | 07/08/2020 | 07/02/2020 |  | 07/01/2020
577 |  | 0 |  |  | Request for Information | Stair Treads/4” Stone Under the Feature | Sheet LL514 detail 6 shows grooves to be cut in the nosing of the cubic stair treads. Is this detail to be used at the historic stair treads at the east entry as well? Sheet LL507 detail 3 shows the addition of a 4” stone under the feature. There is no detail for the profile on the edge of the stone. Is it the same as the corner caps on the east fountain please clarify? |  | Regarding 6/LL514 - that is the preference, to maintain a uniform look on the nosing for each stair. However as the stone detail for the historic stair is still under review, we will need to finalize that direction after it is known if a cubic stone step will work or if it needs to remain as two separate stone slabs for the tread and riser. Regarding 3/LL507 - that is correct, the intent of the stone pedestal cap for both fountains is to match the profile found of the corner caps on 9/LL508. ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 07/01/2020 |  |  |  |  | Closed | 07/08/2020 | 07/07/2020 | 07/07/2020 | 07/07/2020 | 07/01/2020
578 |  | 0 |  |  | Request for Information | Alternative Fix for Short CMU Wall in Area 2 | As an alternate method, rather than a column, could we add a beam from the CMU wall end, continuing East, to the next existing beam (only 3’ out) that would support beam B1072? This would involve adding a wall mount beam clip at the end of the CMU, a new beam, and a clip welded onto B1076. |  | See attached sketch for alternate connection that will allow the use of the same beam. ¦ You are welcome ¦ Zach, thanks for your help. |  |  | Medium | Jay Webster | Westland Construction, Inc. | Structural Engineers |  | 07/01/2020 |  |  |  |  | Closed | 07/08/2020 | 07/08/2020 | 07/06/2020 |  | 07/01/2020
579 |  | 0 |  |  | Request for Information | 3rd Floor Lighting in Initiatory Rooms | Due to multiple building restraints IE. duct work, framing, j boxes ,mech. and sprinkler piping. We are asking for an exception to use MC cable to supply the lighting in the 3rd floor initiatory rooms 309-314 and 321-327. We will pipe the switches together with .75 EMT conduit and run the switch leg in each room to recessed cans in that room with MC cable. This will also allow for future height and side to side adjustment if there is a flexible connection to lights. |  | MC cable will be acceptable at the areas indicated in the RFI ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020 | 07/02/2020
580 |  | 0 |  |  | Request for Information | Sevice outlets in elevator shafts | The elevator shafts are going to require 120v outlets top and bottom of elevator shafts. ELV 1-1 is not showing outlet at either location, ELV 1-2 is showing outlet at bottom but not at top, ELV 2-2 is not showing at either location, ELV 5-1 and ELV 5_2 is showing outlet at bottom but not at top and phone is going to need to be moved from Elevator control rm 502 to elevator shaft where the phone connection is on the elevator equipment. Please Advise |  | Provide outlet at top and bottom of each elevator shaft. Elevators numbers below coordinate with the elevator submittal. Elevator 1 (freight) - Use circuit L1P0D-1 per latest plans. (EP100) Elevator 2 (Lobby 131) - Use circuit L1P0B-27 per latest plans (EP100) Elevator 3-4 (Lobby 185) - Use available circuit in panel L3P1B. Elevator 5 (Lobby 190) - Use available circuit in panel L3P3B. IF phone connection is located in shaft locate phone connection to match elevator requirements. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/23/2020 | 07/17/2020 | 07/08/2020 | 07/02/2020
581 |  | 0 |  |  | Request for Information | West Steel Stair Layout | Please review the elevations in the attached document and advise if they are per the design intent. With the adjustments that have occurred due to the building floors not being level and with this effecting all the levels. |  | Please see attached response. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/02/2020 |  |  |  |  | Closed | 07/05/2020 | 07/15/2020 | 07/14/2020 |  | 07/02/2020
582 |  | 0 | 220000 | P110 | Request for Information | Instruction Room Sink IS-1 at Room 136 | Room 136, wall mounted instruction room sink IS-1, see attached screenshot that indicates the waste line dropping down through a 14" concrete beam at level 0 overhead. Attached is sheet P110 with this shown. | See attached screen shots. Please provide means to install waste at this location for the IS-1. | See Spencer Landeens comments on July 10th. Thanks ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/15/2020 | 07/15/2020 | 07/10/2020 | 07/02/2020
583 |  | 0 |  |  | Request for Information | PR3 option C Plaster over stone | Are there existing door casings that are to remain on level two? If so, how proud are they from the stone? How thick is the plaster at the window splays? Option A and B will have an estimated finished thickness of 2.5" (1 5/8" stud, 5/8" gyp, 1/8-1/4" Plaster) Is the objective, for option C, to build up the plaster the same 2.5" thickness or to apply the minimum to cover the stone? |  | With the understanding that this is an existing building and there will be variations in the dimensions given and that this is to be considered as a general rule for the project. They are: The plaster thickness on the splays for level 2 windows vary from approximately 1 3/8” and 7/8” The door casing around the arches that are staying on level 2 are proud of the stone 5/8” – 1 ¾” |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | Westland PE’s |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/23/2020 | 07/09/2020 |  | 07/02/2020
584 |  | 0 |  |  | Request for Information | Updated Lighting Layout RE: ASI_12 & RFI_535 | ASI_12 and RFI_535 response was to add a soffit around duct below the ceiling in room 315. Now that the ceiling is no longer flat can we get a new lighting layout in that room? |  | Adjust the lighting around the duct work. Verify your backgrounds match latest architectural ceiling plans for this area. |  |  | Medium | Tyson Blatter | Westland Construction, Inc. | Electrical Engineers |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 08/12/2020 | 07/31/2020 |  | 07/02/2020
585 |  | 0 | 220000 | P103 | Request for Information | Level 3 west tower-Electric Water Cooler-Chiller Accessory | Drawing P602, fixture EWC-1 per the attached schedule and submittals indicate installing the drinking fountain chiller within 10' of the fixture. In attempting to locate this chiller serving EWC-1 on level 3 west tower, we have found congested space above the janitor storage room where it is shown to be located, see drawing P103. | See attached drawing and screen shot. We propose locating the drinking fountain chiller at the south wall of the janitor storage room as shown proposed. Please confirm this location is acceptable. | Please see response from Mechanical engineer. ¦ If this is not acceptable will you, please provide an alternate. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/13/2020 | 07/10/2020 | 07/09/2020 | 07/02/2020
586 |  | 0 | 220000 | P110, P101 | Request for Information | Waste piping serving restroom 120a | Waste piping shown to serve restroom 120a at Annex level 1 is conflicting with concrete wall below in storage room. Currently a 6" wall is shown as to be installed at gridline AH. See attached drawing and screenshot for review. | Please advise if an 8" wall at gridline AH level 1 restroom 120a is an option to allow the plumbing waste piping to avoid concrete wall conflicts below. | Your suggestion of making the wall at gridline AH of level 1 restroom 120A to an 8" metal stud wall in order to miss the concrete wall below is fine. This wall is to be 8" metal stud only in this room. Thank you ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/02/2020 |  |  |  |  | Closed | 07/09/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020 | 07/02/2020
587 |  | 0 |  | S100 / AE146 | Request for Information | Cooler-Freezer Slab RE: ASI_16 & CCD_54.4 | The freezer-slab recess was removed as part of ASI_16 on AE146. These changes weren't clouded but now, with the Kitchen being removed in CCD_54.4, this is probably your intent. The recess still appears on S100. | Issue an ASI with an updated S100 or Add the recess being removed from AE146 and S100 to a CCD_54.4 revision. or Just answer the RFI and I'll redline it into the drawings. | See the attached email from Scott G. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/06/2020 |  |  |  |  | Closed | 07/09/2020 | 07/06/2020 | 07/06/2020 |  | 07/06/2020
588 |  | 0 |  |  | Request for Information | 4th Floor Lighting Layout Conflict | See the attached lighting layout for the 4th floor. There are a number of clashes with the ceiling joists. Note: They're a lot less clashes if we move all can lights and chandeliers on the lower ceilings 1" off center towards the outside walls to avoid framing. This plan includes that shift. Please advise if that shift 1" on lower ceilings is acceptable. We need to have further discussion on how to deal with each of the clashes. We will likely need to cut some ceiling joists and will need to account for it structurally. |  | This will be fine to adjust the layout 1" off of center as proposed in the 4th floor to avoid ceiling joists. Thanks |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/06/2020 |  |  |  |  | Closed | 07/13/2020 | 07/08/2020 | 07/07/2020 |  | 07/06/2020
589 |  | 0 | 220000 | S101A | Request for Information | Waste and Vent piping Annex gridline AC and A5 at beam | Waste piping at gridline HD is now conflicting with steel beam layout per attached screen shot per CCD 37R2 direction. We need to avoid the steel beam. Layout of concrete sleeve was completed prior to steel beam shifting and creating this issue. See attached screenshot of issue. | Two options as reveiwed: -Approve steel beam penetration at this location or -Core new hole south of steel beam and patch previously cored hole | Please core a new hole south of the steal beam and patch the previously cored hole. ¦ Please see the comment from Spencer Landeen (VBFA) dated 9-July-2020. The waste piping in question was rerouted as part of CCD-054.3R1 to drop in the double-stud wall between RR [011] and Grab-N-Go [011]. The existing hole is no longer required and may be filled. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/06/2020 |  |  |  |  | Closed | 07/13/2020 | 07/15/2020 | 07/15/2020 | 07/09/2020 | 07/06/2020
590 |  | 0 |  |  | Request for Information | RFI 460 Beam Seat | The angle seat solution provided in RFI 460 contains a few hurdles. The seat is 24" long - but only sits on 9" of material. Is it possible to make this seat 9" long? It also conflicts with an existing bolt - can the seat be cut down to a 5" leg on the vertical face in order to accommodate? See attached screen shot for clarification. |  | In lieu of cutting the leg down to 5" please drill a hole in the leg to accommodate the interfering bolt? This hole could be oversized to allow for in-field adjustment. ¦ Partial Answer: The I-Beam will be installed in the current location of the wood beam, so we will need the 24” long seat. Remaining Question: It conflicts with an existing bolt - can the seat be cut down to a 5" leg on the vertical face in order to accommodate? See attached screen shot for clarification. |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 07/07/2020 |  |  |  |  | Closed | 07/14/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020 | 07/07/2020
591 |  | 0 | 220000 | P110, P301 | Request for Information | Structural Pipe Penetrations Detail | Drawing P110, Keynote #38, grid line AB between A3 and A4, states to sleeve piping through middle third of structural beam, coordinate penetration with structural per detail 2 on P301. See attached for review. Structural drawings do not appear to have any details for this application. | Please provide a structural detail for this application. See attached clouded drawings for clarification. | No additional reinforcement is required at these specific beam penetration locations. Please locate holes in the middle third of the beam web height. These holes are to be drilled into the beam and NOT cut using a torch. Reinforcement will be required if the holes are cut using a torch. Please advise if a torch will be used. ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Structural Engineers |  | 07/07/2020 |  |  |  |  | Closed | 07/14/2020 | 07/29/2020 | 07/23/2020 | 07/08/2020 | 07/07/2020
592 |  | 0 | 220000 | P111, P106 | Request for Information | Annex Loading Dock Roof Drains | Drawing P111 indicates a 2" RD and 4" ORD serving the annex loading dock roof. Drawing P106 roof layout indicates 6" RD and 6" ORD sizing. | Please advise if the sizes shown on drawing P111 are correct or if the sizes on P106 are correct. See attached marked up drawings for clarification. | See Spencer Landeens comments. Thanks ¦ ¦ ¦ ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 07/07/2020 |  |  |  |  | Closed | 07/14/2020 | 07/16/2020 | 07/15/2020 | 07/10/2020 | 07/07/2020
593 |  | 0 |  | LI101 | Request for Information | Pot Irrigation LI101 | Per LI101-Irrigation plan, Irrigation is missing to the pot in the photo radius area. Through phone conversations the pots need to be on their own valve. Please provide direction for the irrigation requirements needed for the pot. Costs are anticipated for this work. Please advise. |  | Please see our response in the attached pdf. Please provide information as requested. Thanks, ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Rob Stratton | Stratton & Bratt Landscaping | 07/07/2020 |  |  |  |  | Closed | 07/14/2020 | 08/20/2020 | 07/08/2020 | 07/16/2020 | 07/07/2020
594 |  | 0 |  |  | Request for Information | Needle Beam Channels & Beams | Please refer to the attached marked up detail 1/S248. We are in need of stiffener clarification for the beams and channels at the interior stone columns. Also - please note that the micropiles are not set square to the jacket walls (see sketch "micropile skew"). Please clarify whether the beams are to align with the jacket walls (beam on right) or with the micropiles (beam on left) |  | The alignment shown in the left side of the "micropile skew" sketch follows the intent of the design. The channels are to be square with the stone column and the w-beams will align where they may depending on micropile location. See attached sketch for stiffener plate clarifications. ¦ Please note that the C Channels will rest on top of an I-Beam, that will be on top of the Micropile. This I-Beam will allow for the C Channels to be installed tight to the Existing Stone Columns. |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 07/07/2020 |  |  |  |  | Closed | 07/14/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020 | 07/07/2020
595 |  | 0 |  |  | Request for Information | CCD 040 Flooring/Base Clarifications 1 | Finish Schedule AE660 calls out BC1 base (carpet) with wall base detail C4/AE570 (from Addendum 3). However, detail C4/AE570 is stone base with a hardwood cap. Which base material is correct? Finish Schedule AE660 calls out WT4 on the south and west walls in room 007, but there is no WT4 in the Finish Legend. Please correct. Finish Schedule AE660 calls out BR3 base (rubber) with wall base detail C1/AE570, but that detail specifies stone base with a hardwood cap. Which base is the correct material? |  | Need clarification on two room names. Response will also be issued in upcoming CCD ¦ Please the names of the two rooms in question. |  |  | Medium | Nathan Gheen | GLOBAL STONE & TILE LLC | Nathan Gheen | GLOBAL STONE & TILE LLC | 07/08/2020 |  |  |  |  | Closed | 07/14/2020 | 09/23/2020 | 09/02/2020 | 09/15/2020 | 07/08/2020
596 |  | 0 |  |  | Request for Information | CCD 040 Flooring/Base Clarifications 2 | Finish Legend shows FT4 and WT3 tile colors as TBD. Please provide these details as tiles can vary in price. Finish Legend shows FS3 as being removed from the project. Drawing AE160B still shows an Ashlar pattern on the floor below Stair 4. Is this flooring to be FS1? Finish Schedule AE660 calls out BT3 base in the Elevator Lobby 053, but Stair Lobby 052 calls out BR3 base. Should these two areas have the same base? |  | Tile colors pending wood floor submittal to coordinate colors. Answered other questions. This is to be issued in an upcoming CCD ¦ I have attached the sample submittal for the flooring submittal as file 096400.02.00 - WOOD FLOORING (Selection Samples). |  |  | Medium | Nathan Gheen | GLOBAL STONE & TILE LLC | Interior Designer |  | 07/08/2020 |  |  |  |  | Closed | 07/14/2020 | 09/24/2020 | 09/15/2020 | 07/08/2020 | 07/08/2020
597 |  | 0 |  | S100B , S245 | Request for Information | Door Fill in Baptistery Grids HB and H2 | Please advise if the door opening on the South East area of the level .5 is to be filled in with concrete or just covered with plaster as discussed in OAC. The Drawings are still showing the doorway as having a concrete sleeve being poured in it. For reference I have attached the drawing that call this out. |  | Per ARW Construction Observation Report 23 Item 23-4, this opening is to be infilled per detail 10/S240. It is true that the drawings currently show a doorway, but this will be revised to show an infill and will be included in a forthcoming CCD. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 07/08/2020 |  |  |  |  | Closed | 07/15/2020 | 07/08/2020 | 07/08/2020 |  | 07/08/2020
598 |  | 0 |  |  | Request for Information | WAP location and mounting | There are WAP'S (wireless access points) shown at the barrel ceilings level 2,3,and 5 is it the intent to have the WAP'S above the ceiling in the accessible attic or bellow? WAP'S where there isn't accessible attic should they be located above ceiling near access doors or below ceiling? What type of box do they mount to? please advise |  | WAP locations should not be located at barrel ceilings within the space but above the ceiling at accessible locations indicated on drawings. WAP locations to be installed per EC details 8, 9, 10 on sheet EC501. Provide blank cabling and blank cover plates. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 07/08/2020 |  |  |  |  | Closed | 07/15/2020 | 07/28/2020 | 07/27/2020 | 07/08/2020 | 07/08/2020
599 |  | 0 |  |  | Request for Information | SwitchGear MS meter | SwitchGear MS is provided with a powerlogic meter capable of tying to network (may need additional accessories or software) Do we need a data connection from MDF to meter? please advise |  | yes, the data cabling and ability for meter to tie into network for remote access and tracking. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 07/08/2020 |  |  |  |  | Closed | 07/15/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020 | 07/08/2020
600 |  | 0 |  | LL514 / AE341 | Request for Information | NE Annex Concrete Stair Detail RE: CCD_68 | Would you like the 1/4" deep saw cut step detail on the exterior stairs on the North East of the Annex (AA-AB / A7-A8)? The detail that was added in CCD_68 doesn't apply to that stair. (see the two details attached) |  | The detail for the north/east exterior stair will not have grooves at the treads and shall be as per the detail with a 1/2" radius edge and broom finish. The Grooves shown on the other details are still up for discussion and may also be omitted. ¦ ¦ Kyle, thanks for the quick response. Have a good weekend. |  |  | Medium | Jay Webster | Westland Construction, Inc. | Landscape Architects |  | 07/08/2020 |  |  |  |  | Closed | 07/15/2020 | 07/16/2020 | 07/10/2020 | 07/08/2020 | 07/08/2020
601 |  | 0 |  |  | Request for Information | Landscape/Site footings detail clarification | 1) Sheet LL502- Detail 5 seat wall and detail 6 retaining wall- what is the reinforcement requirement for note 5 in these details? 2) Detail 1/LL502- any reinforcement required in the 8"x18" bench footings? 3) Detail 7,8/LL502- is all the rebar in the stair footings epoxy coated? See note 10 on detail 7 or just the stone stairs? East fountain sheet LL506 4) 3/LL506 the typical fountain walls for note 5 do not give the typical footing size and reinforcement requirement. Please provide. Do the walls and footings sizes match the north fountain plan on LL507 (6" walls, 2'-6"x1'-0" footing)? 5) 2/LL506 please confirm the 6" fountain slabs and thickened are not reinforced? North fountain sheet LL507 6) 2/LL507 what is the reinforcing requirement in the footings (note 5) 7) 3/LL507 please confirm the 6" fountian slabs and thickened footings are not reinforced? 8) 2/LL508 note 3 please provide footing size and reinforcement requirement for the corner sections? (wall reinforcement provided) Monument sign LL510 9) 4/LL510 Column and wall section. Please provide size of footings and reinforcement requirement |  | See updated details issued in CCD-077 ¦ After discussion with ARW yesterday, epoxy coated rebar is not required at the stairs. ¦ For question #3 please clarify if stair detail 8/LL502 is epoxy coated rebar or black rebar. Based on note 10 on 7/LL502 we assume it is epoxy coated only at the stone stairs. All other questions are clear in CCD 77. |  |  | High | Judd Bundy | Innovative Concrete LLC | Landscape Architects |  | 07/08/2020 |  |  |  |  | Closed | 08/03/2020 | 09/14/2020 | 09/11/2020 | 07/08/2020 | 07/08/2020
602 |  | 0 |  |  | Request for Information | Landscaping / Mechanical | Existing conditions are described in RFI 413. There are two - 2” meters that supply the entire site with water. The water supply enters the site via two - 2” poly lines that connect to one 4” main water line. Both Landscaping and Mechanical say they need 4” to supply their systems. Do the existing 2 – 2” meters supply the water needs for the building and the landscaping needs? Does the attached picture describe what needs to be built? Does the water connections need to be in a vault? Or can the vault be demoed with access to the valves? | Connect the two- 2” poly lines into one 4” line. From that 4” line it would (T), one supplying the landscaping and one supplying the building ( see attachment ) | This question is for the civil engineer and the owner. ¦ The vault can stay in place. The idea is that one of the 2" water meters would be for irrigation. Inside the vault, the water line would change from a 2" line to a 3" line and would leave the vault to the north and connect to a 3" irrigation backflow preventer. This backflow preventer is one that the temple facility groundscrew has on-site. We would recycle it. The other 2" water line that comes from the other 2" water meter would change from a 2" to a 4" (PVC C-900) inside the vault. It would leave the east end of the vault and connect to the building. There is an existing 1.5" water meter that leaves 400 South and connects to the site in the NE corner. This water meter would be relocated to come off the proposed waterline in 300 East and connect to the site on the east end. This water meter would be used for irrigation. Attached is a concept drawing that shows this. Once this is all approved by the team, a CCD will be issued. ¦ We have reviewed the C.11 drawing and provided responses in the attached 18-117 RFI 602 Response MGBA 200730. We have provided solutions for pipe sizing and pointed out items to be included and coordinated. Thanks, ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Brandon Ruiz | MGB+A The Grassli Group | 07/30/2020 |  |  |  |  | Closed | 07/15/2020 | 08/13/2020 | 07/30/2020 | 07/23/2020 | 07/09/2020
603 |  | 0 |  |  | Request for Information | Humidity and Duct Detectors | The steam generators will be introducing humidity into the ducts. Both the mechanical contractor and fire alarm contractor said this has been a problem on previous jobs causing the duct smoke detectors to go into alarm. Please advise if any changes need to be made to the fire alarm system. |  | Duct Smoke Detectors are required to meet code. Are photoelectric type duct smoke detectors or ionization type detectors being used? Photoelectric type may reduce the issue. Locate them as far from humidifier equipment as possible and still meet code requirements. Can they be located at least 10ft or more from humidifiers? Can the levels of humidity be reduced or humidifier connection made downstream of detector? What solutions/changes were made on the past projects mentioned to resolve these similar issues as was noted? Does the mech/fire alarm installer have any additional recommendations for the design team to meet code yet reduce the issues noted? ¦ See comment from Brian Oswald, VBFA dated 25-August-2020 ¦ ¦ Please see this RFI regarding the duct smoke detectors. ¦ The duct smoke detectors on this project are photoelectric type. We will put as much separation as we can between them and the humidifiers. As far as reducing humidity levels or locating the connection downstream of the detector, that would be a question for US Mechanical/VBFA. Both US Mechanical and AAA Fire said previous solutions were to eliminate the duct smoke detectors and provide smoke detection throughout the entire building, which would be pretty extensive on this project. |  |  | Medium | David Barney | Wilkinson Electric Inc | Mechanical Engineers |  | 07/09/2020 |  |  |  |  | Closed | 07/16/2020 | 08/26/2020 | 08/25/2020 | 07/14/2020 | 07/09/2020
604 |  | 0 |  |  | Request for Information | Demo Floor Around Hist. Elevator | Please advise if the existing flooring around the elevator needs to be removed then reinstalled and new LVL's and ¾” Tongue and Groove Flooring. For reference I have attached some drawings showing this condition. |  | Structurally, the intent was to only remove the floor in the immediate location of the new elevator shaft. All other floor framing and sheathing was to remain in place. ¦ The instruction to removal this portion of the floor is in CCD-11R.11 and is waiting for the contractor to sign. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/09/2020 |  |  |  |  | Closed | 07/12/2020 | 07/13/2020 | 07/13/2020 |  | 07/09/2020
605 |  | 0 |  | S101, S102 | Request for Information | Historic Stair 5 | In reviewing the stair 5 we found the following questions and have discussed them with Matt McBride on site. Please advise on the following questions; 1. Is the section of jacket wall along the North of stair 5 Is this section of Jacket wall to be installed 6-1/2" below 100 or are we to install is at 6-1/2" below 95-1" 2. Please advise as to what this post North West of Elevator saving Lobby 190 consists of Steel Size/Concrete and embed placement. As well as attachment method. 3. Please show sizes of posts just South of gridline H5 between grid line HC and HB. All the questions above are expanded upon in the attachment. |  | See attached for ARW Responses. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 07/09/2020 |  |  |  |  | Closed | 07/12/2020 | 07/10/2020 | 07/09/2020 |  | 07/09/2020
606 |  | 0 |  |  | Request for Information | PR# 4 Door types level 3 and 5 | New door type # 2 AE 610 call for new door to be 6'-8" . Door type 2on new door schedule AE 602 call for doors to be 7'-0" high. Which is correct Detail A3 shows flat portion of the door casing to be flush with the plater wall. Based on our door conversation casings wood base are all to be applied after drywall or plaster. |  | Door type #2 height needs to be 6'-8". The baseboards and casing are to be installed after, per conversations. Thanks ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 07/10/2020 |  |  |  |  | Closed | 07/17/2020 | 07/15/2020 | 07/15/2020 | 07/13/2020 | 07/10/2020
607 |  | 0 |  |  | Request for Information | Custom Tile | 1 In the fountains there is some 6 x 6 custom made tile. Is the final design approved for fabrication? 2 Is there a need to have additional samples of the approved design submitted prior to fabrication release? |  | 1 In the fountains there is some 6 x 6 custom made tile. Is the final design approved for fabrication? Yes, the team has approved the design and have notified the manufacturer on the final design and colors of the tile. Please also note the attached image that provides desired orientation of the tiles for installation. 2 Is there a need to have additional samples of the approved design submitted prior to fabrication release? Yes, please contact the manufacturer to have three tiles made for a submittal to approve final colors and color consistency. ¦ ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 07/10/2020 |  |  |  |  | Closed | 07/17/2020 | 07/23/2020 | 07/17/2020 | 07/16/2020 | 07/10/2020
608 |  | 0 |  |  | Request for Information | Blind Side Waterproofing | Is blind side waterproofing needed here (see the attachment)? The red checkered area was omitted. |  | See CCD-074 for instructions and recommendations from Morrison Hershfield. |  |  | High | Carter Cluff | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/10/2020 |  |  |  |  | Closed | 07/16/2020 | 07/20/2020 | 07/17/2020 |  | 07/10/2020
609 |  | 0 |  |  | Request for Information | West tower slab elevations ASI 11 and 33 | See attached mark ups from ASI 11 and updated information from ASI 33. 1) Please verify our understanding of the changes to top of concrete elevations at the slabs in ASI 033? 2)Also please confirm 2" recess elevations in locations as noted on attachments. ASI 11 Top slab ASI 33 Top slab Level 0 79'-0" 79'-0" Level 0.5 88'-9" 88'-9" Level 1 100'-0" 100'-0" Level 2 111'-7" 111'-3 1/2" Level 3 130'-2 1/2" 130'-1" Level 4 141'-4 3/4" 141'-3 3/4" Level 5 160'-1 3/4" 160'-0 3/4" Roof/ TOW 173'-3 1/2" 173'-3 1/2" |  | The attached recessed slab areas at the west addition restrooms and janitor closets match what CRSA understands are the correct elevations that were given by the contractor. The slab thickness in those areas will be reduced from 10" to 8" thick to achieve the 2" depression. Please refer to the future ASI 033-R.1 for the structural clarifications regarding this condition. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 07/13/2020 |  |  |  |  | Closed | 07/20/2020 | 07/28/2020 | 07/27/2020 | 07/13/2020 | 07/13/2020
610 |  | 0 |  |  | Request for Information | Basement Mechanical Openings | The Openings in the basement are bigger then the plans showed on the bid set AD100A scaling the plan we came up with the wall being 6'6'' thick on the north east 4' on the north west and west side and 6'6" on the south side. but. the top of the opening is 7' thick and the base ranges from 11' to 13' thick. there we be a change in price on these openings with saw cutting and demo how do you want us to proceed with the schedule we are being pushed to keep moving |  | What TID is saying seems to be true. This needs to be worked out with Westland and the subcontractors. ¦ OK, Thanks for the heads up. ¦ This is resulting from unforeseen circumstances. ¦ That is true but i want to make sure you understand there are going to be additional costs incurred due to the increased thickness of the existing foundation wall. |  |  | High | Travis Keenan | TID, Inc. | CRSA ARCHITECTURE |  | 07/14/2020 |  |  |  |  | Closed | 07/18/2020 | 07/29/2020 | 07/28/2020 | 07/14/2020 | 07/14/2020
611 |  | 0 |  |  | Request for Information | CCD 040 Stone and Tile Clarifications | 1. Finish Schedule AE660 calls out BC1 base (carpet) with wall base detail C4/AE570 (from Addendum 3). However, detail C4/AE570 is stone base with a hardwood cap. Which base material is correct? 2. Finish Schedule AE660 calls out WT4 on the south and west walls in room 007, but there is no WT4 in the Finish Legend. Please correct. 3. Finish Schedule AE660 calls out BR3 base (rubber) with wall base detail C1/AE570, but that detail specifies stone base with a hardwood cap. Which base is the correct material? 4. Finish Legend shows FT4 and WT3 tile colors as TBD. Please provide these details as tiles can vary in price. 5. Finish Legend shows FS3 as being removed from the project. Drawing AE160B still shows an Ashlar pattern on the floor below Stair 4. Is this flooring to be FS1? 6. Finish Schedule AE660 calls out BT3 base in the Elevator Lobby 053, but Stair Lobby 052 calls out BR3 base. Should these two areas have the same base? |  | Please provide room names on some questions ¦ Please see CCD 040r1 and PR7 ¦ ¦ ¦ will you please provided the room numbers associated with the questions in this RFI. ¦ 1. Please clarify room name. Rooms Office 008, Worker Lounge 009, Worker Training 015, TFM Dressing 017, TFM Womens 018, Laundry Supervisor 031, TFM Office 045, TFM Mens 046, and TFM Dressing 047. 2. Please clarify room name. Custodial Supply Office 007. 3. Please clarify room name. Rooms Vestibule 005, Break Room 010, Grab-N-Go 011, Hall 019, Hall 023A, Hall 023B, Vestibule 024, Stair 1 Lobby 024B, Vestibule 025, Laundry 028, Hall 044, Vestibule 049, Vestibule 050, Hallway 051, Stair Lobby 052, Stairwell 068, Electrical 183, Electrical 302, Electrical 315, Data/Telecom 402, Elevator Control Room 502, and Electrical 515. 4. Answered in RFI 596. - Answer in upcoming CCD, according to RFI 596. 5. Answered in RFI 596. No answer found on RFI 596. 6. Answered in RFI 596. No answer found on RFI 596. |  |  | Medium | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 07/14/2020 |  |  |  |  | Closed | 07/21/2020 | 11/10/2020 | 10/29/2020 | 09/24/2020 | 07/14/2020
612 |  | 0 |  |  | Request for Information | CCD 54.4 Stone and Tile Questions | 1. The drawings show many changes to the layout of the walls. Please update the door schedule to reflect the stone threshold changes. 2. Drawing AE4004 from CCD 54.4 shows a countertop in Custodial Supply Office 007. Is this countertop stone? If so, please specify the type and provide details for the edge profile, thickness, etc. 3. Drawing AE4002A from CCD 54.4 shows countertops in Break Room 010 and Grab-N-Go 011. Are these countertops stone? If so, please provide the same details as listed in question 2. |  | Please see answer on finish and edge profile. CRSA to update drawings for clarification |  |  | Medium | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 07/14/2020 |  |  |  |  | Closed | 07/21/2020 | 09/08/2020 | 09/03/2020 | 07/16/2020 | 07/14/2020
613 |  | 0 | 233519 |  | Request for Information | Sealant at dryer exhaust | Specification section 233519, subsection 2.2, paragraph E states to use a 3M EC-750 sealant to seal the dryer exhaust system duct. Upon further investigation, it has been determined that this particular product as listed in the specifications for this type of application is no longer available and manufacturing has been discontinued. | Please provide an alternate sealant to install the dryer duct system. | Please provide a sealant that has been used in this application on other projects. If this is a new application, please reach out to your supplier and get his recommendation. Then I will need you to fill out the Equal Product Approval Request Form. For your convenience I have copied a link to it bellow. https://studio.bluebeam.com/share/j24an3 |  |  | Medium | Justun Bylund | US Mechanical LLC | Westland PE’s |  | 07/14/2020 |  |  |  |  | Closed | 07/21/2020 | 07/16/2020 | 07/15/2020 |  | 07/14/2020
614 |  | 0 | 265100 | EL100C, EL101B, EL101D | Request for Information | LS4C Lights in Rest Rooms | Restrooms 070, 080, 134, and 152 show a type LS4C light fixture which is a 1x4 wrap-around. They are shown located close to the wall, almost in the corner. How far from the wall should these be mounted? And please confirm this is the correct light fixture. |  | That is the correct fixture type. They should be mounted 2’ from the wall. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 07/15/2020 |  |  |  |  | Closed | 07/22/2020 | 07/22/2020 | 07/22/2020 | 07/15/2020 | 07/15/2020
615 |  | 0 |  |  | Request for Information | 4th Floor Ceiling North/South Wings | Please confirm what is going to happen with the joint between the historical crown molding and the new ceiling that will be installed on the wings. I have drawn up my understanding of that it is going to consist of but the items we are specifically looking for are: 1. Specific location of where the Crown is to be cut. 2. Attachment method of the Drywall to the Crown Molding. 3. Size of gap from the Drywall to the existing Crown Molding |  | Please discard the detail that was provided with this RFI. Please see the newly attached detail. The historic plaster crown moldings on the far north and south walls have been demolished and will be replaced with a like GFRG crown molding. The historic plaster crown at the column line and entablature is to remain, and be repaired as needed. as discussed on-site with sub contractors, the new suspended gyp ceiling will be hung at a height as to provide the minimum space required for MEP items. at the transition of the gyp ceiling and the crown molding(s) please provide a 'mudded L-bead' and a 3/16" gap between the two. Please fill gap with paintable caulking. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/22/2020 |  |  |  |  | Closed | 07/25/2020 | 08/11/2020 | 08/11/2020 |  | 07/22/2020
616 |  | 0 |  |  | Request for Information | Rebar Around Buttress A7 / AH | The typical buttress rebar wont work for the buttress near A7 / AH. Please advise (note see the attached suggestion). |  | The suggested detail for this is acceptable. Judd Bundy and Brent White spoke about this on site this morning and discussed the same detail. |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 07/22/2020 |  |  |  |  | Closed | 07/27/2020 | 07/23/2020 | 07/23/2020 |  | 07/22/2020
617 |  | 0 |  |  | Request for Information | Annex / Addition Bldg - Interior Windows Types AA & BB | During the H2 window mock-up review and subsequent meeting on Tuesday, July 14, we (Scott Gilberg, Ryan Thomas, Re-View) discussed the potential of changing the wood species of the interior window types (AA and BB) at the Annex. We discussed changing from Accoya to Sapele Mahogany to provide a finish substrate that is more in line with other interior elements. Please confirm that this is the direction that we need to proceed. We consider this to be a no cost change. |  | this proposal to move to mahogany for the windows mentioned is acceptable ¦ |  |  | High | Todd Maxwell | Re-View Windows, Inc. | CRSA ARCHITECTURE |  | 07/23/2020 |  |  |  |  | Closed | 07/31/2020 | 08/13/2020 | 08/11/2020 | 07/23/2020 | 07/23/2020
618 |  | 0 |  |  | Request for Information | Addition level 1 Floor Boxes | Dimension floor outlet plan shows 4 additional floor boxes 2 at the recommend desk and 2 in room 132a . the electrical drawing shows standard outlets. Which is correct? Matron office 120 We need wall dimensions or the floor box dimensions to be taken off grid line. |  | 1a - The 2 locations show at the recommend desk can just be conduit stub ups as the wiring will be routed inside the millwork to their final locations. Follow Envisions drawings. 1b - The 2 locations at room 132a can be omitted, follow Envisions drawings to run wiring in walls and put the power/data just under the countertop for the point of sale. 2 - Matrons Office, 3' - 2 1/2" South of Grid A7, 16' - 3" East of Grid AH ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Jeff Adams | CRSA ARCHITECTURE | 07/27/2020 |  |  |  |  | Closed | 08/03/2020 | 07/28/2020 | 07/27/2020 | 07/27/2020 | 07/27/2020
619 |  | 0 |  |  | Request for Information | Clear & Grub Sod Areas | After digging in some sod areas with existing trees we have become more aware of the extensive root systems of the trees. We believe removing six inches of topsoil and replacing it in this area would be very detrimental to the existing trees because it would damage many roots. We think the minimal impact we could have on the trees while still providing a great product for the customer would be to only sod cut the top one inch of soil and remove the sod. Then just topcoat the area with about one inch of topsoil as needed and lay new sod. |  | Please see our response in the attached document. ¦ |  |  | Medium | Jayson Christensen | Stratton & Bratt Landscaping | Landscape Architects |  | 07/28/2020 |  |  |  |  | Closed | 08/04/2020 | 08/18/2020 | 08/11/2020 | 07/28/2020 | 07/28/2020
620 |  | 0 |  |  | Request for Information | Mainline PSI | The pressure in the mainline is very high at up to 130 psi and fairly steady at 113 psi. Most parts in the irrigation system have a manufacturers warranty that states the pressures should be between 35 and 90 PSI. We believe a pressure reducing valve at the point of connection may be needed to reduce pressures to 90 psi. Currently on the project there are a Netafim drip valves that make a high pitched noise because of the high pressure. Two of the valves have also had to be replaced and frequently tightened to resolve leaks that are developing. We believe the noise and leaks are as a result of the high pressure. A pressure reducing valve could be installed by the point of connection and should likely be 2" or larger. Please advise on a possible solution. |  | See attached response from 8/11 ¦ Please refer back to our original answer from 8-11-2020 which was uploaded as a PDF document. ¦ ¦ I believe the question of adding a PRV for the irrigation lines would fall to the court of the landscape architects (or possibly the civil engineer). |  |  | Medium | Jayson Christensen | Stratton & Bratt Landscaping | Landscape Architects |  | 07/28/2020 |  |  |  |  | Closed | 08/04/2020 | 10/01/2020 | 09/22/2020 | 09/22/2020 | 07/28/2020
621 |  | 0 |  |  | Request for Information | 4th floor lighting on lower ceilings | Confirm lighting layout modification on 4th floor (as shown on attachment) per conversation with Scott Gilberg, Ben Rogers, and Kyle Welch on July 28 2020. | Adjust can light layout to avoid clashes with joists and plumbing . | the proposed direction provided on the sketch is acceptable. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 07/30/2020 |  |  |  |  | Closed | 08/03/2020 | 08/12/2020 | 08/11/2020 | 07/31/2020 | 07/30/2020
622 |  | 0 |  |  | Request for Information | Generator Pad | Detail 2/ES503 shows a 12" housekeeping pad for generator 6" above grade 6" below grade. this generator is located on a suspended slab is the 12" pad necessary or could we use a 4" slab doweled into the suspended slab? The original generator at this location was on a 4" pad, Does the additional weight of the larger pad and generator need to be considered? please advise |  | The housekeeping pad for the generator at this specific location should be no more than 4" thick and should be reinforced similar to those pads in the basement of the north addition. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 07/30/2020 |  |  |  |  | Closed | 08/06/2020 | 08/10/2020 | 08/06/2020 | 07/31/2020 | 07/30/2020
623 |  | 0 |  |  | Request for Information | Cut Columns on North Wall of Stair | Please confirm that, per conversations held while preforming site walks, that the stone column as shown in the attached drawing are to be cut flush with the adjacent wall. This column does not have any weight bearing on it from above. |  | Confirmed. Please see ARW Report #28, Item 28-7 |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/05/2020 |  |  |  |  | Closed | 08/03/2020 | 08/10/2020 | 08/06/2020 |  | 07/31/2020
624 |  | 0 |  |  | Request for Information | LVL Spacing 2nd and 0.5 Levels | Please advise if we are going to need to add additional backing in the locations that are spaced further then 24” due to ducting that has been installed. For reference I have marked on a Drawing the locations this greater than 24” spacing is occurring. |  | Please refer to ARW Report #28 Item 28-5 for information on this matter. ¦ Please see forthcoming CCD #080. (wall type will be changing to add a layer of plywood in lieu of a layer of sheet rock) this to handle the large spans between studs ¦ Field report 028-5 says "Westland asked if the sheetrock needs additional backing where the studs are spaced further apart than 24” o.c. This has been discussed previously and it is our understanding that CRSA will issue an ASI outlining how this should be handled." |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/05/2020 |  |  |  |  | Closed | 08/07/2020 | 08/11/2020 | 08/11/2020 | 08/10/2020 | 07/31/2020
625 |  | 0 |  | LI101 | Request for Information | 2” main irrigation line in area A | (Marked in Blue) The communication wires do not work. Currently the new communication wire is on top of the ground that connects the clock to the valves. New wire needs to be installed to these valves underground. With the issues of the main irrigation line around the Visitor Center, there is a concern there are issues with this main line. (Marked in Red) The 2” main irrigation line crosses under the fire lane into the planter area next to the historical temple. Is there a need for the main line to extend under the fire lane? Or can it be located further away from the temple? The concern is having the main irrigation too close to the temple and the damage that may happen if a main irrigation line break. Irrigation lines have been broke with maintenance work and equipment in the past. | Relocate the drip line valves to the opposite side of the fire lane and have a drip supply line sleeved under the fire lane | The drip valves and mainline in question have not been shown on that side for quite some time. The contractors must not have the correct set of plans. Please verify that the contractors (both general and irrigation) have the most recent plan set. The CCD-006R2 is the most recent official drawing set prior to the 400 south Permit Set. Please refer to CCD-006R2 as the most recent approved set for irrigation. These were issued in February of 2020. ¦ New responses have been added. Please review the new descriptions and markups. ¦ Valves located in this area previously are to be installed in this same general area (blue box). If tree roots are found to interfere with this location please adjust the valves to avoid tree roots to the red box areas. The contractor is to adjust location(s) as needed in field to avoid roots as necessary. If lateral line excavations can be reduced by relocating to the red boxes this is also acceptable. Follow all previously released precautions included in the tree preservation notes and specifications. Provide as-built drawings of final valve locations upon completion. ¦ ¦ The 2" irrigation main line (marked in blue) is existing and is not to be replaced. But the communication lines are not functioning and will not communicate with the clock. New wires are connected but are ran on the surface. Connecting these wires underground may be additional work and if these wires are to be connected underground Should the old main line and valves be replaced? |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 09/10/2020 |  |  |  |  | Closed | 08/07/2020 | 09/22/2020 | 09/10/2020 | 07/31/2020 | 07/31/2020
626 |  | 0 |  |  | Request for Information | Sewer, Landscaper shed sewer elevation and sewer line connec | (#1 Blue cloud) The 6” line connecting to the 400 South from the dock area is showing that it connects directly to the 8” that runs along 400 South. Is the intent for the 6” sewer line connects to the 8” or should it be connected to SSMH#04? (#2 Blue cloud) The clouded area #2 is missing elevations. These elevations are needed for the work to proceed. |  | #1. One of the comments from the JUC was that they didn't want laterals connecting at the manhole. They want it to connect in the mainline. #2. Attached is the pdf that has the sewer elevations for the landscaper's shed. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 07/31/2020 |  |  |  |  | Closed | 08/07/2020 | 08/13/2020 | 08/05/2020 | 07/31/2020 | 07/31/2020
627 |  | 0 |  | AE 660, thru AE 662 | Request for Information | CCD 040 Floor Finish Schedule | Change to the finish schedule show contradictions in the base type. A few examples are. Rm. 011, 019, 023A, 023B, 024, 044, 049, 050, 051, 052, call for wall base type C1/AE570 wood base cap on top of stone and the Base Finish calls for BR3 which is rubber base. I have not reviewed all the finish schedule to see if other errors occur. Clarify which is the correct wall base type. |  | Please reference CCD 040r1 and PR7 ¦ ¦ |  |  | High | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 07/31/2020 |  |  |  |  | Closed | 08/16/2020 | 12/02/2020 | 10/29/2020 | 08/12/2020 | 07/31/2020
628 |  | 0 |  |  | Request for Information | Concrete sidewalk dowels needed for the 2 part pour | To accomplish the banding design on the sidewalks, the sidewalk banding is poured first and the middle section is poured later. This approach has been discussed and approved by the architects. In field discussions between Westland and CRSA, CRSA has requested that the sidewalks from now on have a rebar hook poured in between the banding pour and center pour. Please confirm and describe type of J hook or dowel needed for the sidewalks. Costs may be associated with this work. |  | Please see our attached response. ¦ ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 07/31/2020 |  |  |  |  | Closed | 08/07/2020 | 08/13/2020 | 08/13/2020 | 08/12/2020 | 07/31/2020
629 |  | 0 |  |  | Request for Information | Historic East Tower Crawl Space Slab and Penetrations | Please reference the attached notations to sheet S100A. 1) Please confirm that we are to install a 12” concrete slab at the crawlspaces beneath confirmation rooms 063 and 064 as noted in yellow in the attached S100A. 2) Please confirm that we are to widen the duct openings through the foundations as shown in the attached S100A. (BIM coordinated shop drawings from US Mechanical have also been included for reference). |  | see response from structural engineer ¦ ¦ 1) This is the direction given by the owner during the site walk on August 30, 2020. This revision will be shown in CCD 45-R.4 2) It is acceptable to widen the duct openings as shown. This is consistent with the conversation between Matt McBride and the team during his site visit. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 07/31/2020 |  |  |  |  | Closed | 08/07/2020 | 08/13/2020 | 08/11/2020 | 08/03/2020 | 07/31/2020
630 |  | 0 |  |  | Request for Information | Brides exit drinking fountain drain | C.9 has a drinking fountain in the brides exit area. The drain for this drinking fountain connects to the sewer line on 300 East. Is it beneficial for the drinking fountain drain to connect to SSCO #03 that is north of the drinking fountain? If the drinking fountain needs to stay connected to 300 east please confirm? |  | This can connect to SSCO#3. The sewer line in 300 East will be abandoned. ¦ ¦ This RFI concerns the sewer line from the exterior drinking fountain in the Bride's plaza. The plumbing drawings indicate an invert for the sewer but that is it. I am assuming that the sewer line routing is shown on the civil plans. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 08/03/2020 |  |  |  |  | Closed | 08/10/2020 | 08/13/2020 | 08/13/2020 | 08/12/2020 | 08/03/2020
631 |  | 0 |  |  | Request for Information | Door schedule question resulting from CCD54.4R2 revised door | Missing from door schedule Door 015D room 012, Door 060A room 060 was on previous schedule, Door 065B is listed as type 4 per meeting notes this was to be type 6 elevation C4/AE4023 to match door 060A with type C4 C1 casing, Door 0190A list door type 31 which does not exist should be type 8 see elevation C1/AE47124 |  | Door 015D is not in the project Door 060A has been removed, no closet in room 060 Door 065B is now Type 4 (supersedes meeting notes to be type 6) Door 190A should be Type 8, this has been corrected ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 08/03/2020 |  |  |  |  | Closed | 08/10/2020 | 08/20/2020 | 08/20/2020 | 08/04/2020 | 08/03/2020
632 |  | 0 |  | Furniture Drawings, RFI 361 | Request for Information | Floor Box Furniture Coordination | As we are laying out the floor boxes as dimensioned in RFI 361, it appears there will be furniture directly above the floor boxes in several location. See furniture drawings. Will there be enough clearance between the floor boxes and the furniture called for in these areas? This is a general question for all floor box locations. Please advise. |  | Please see CCD-050 revisions 1, 2 and 3 for revised floor box locations. |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/04/2020 |  |  |  |  | Closed | 08/04/2020 | 08/20/2020 | 08/20/2020 |  | 08/04/2020
633 |  | 0 |  |  | Request for Information | Fabric for altars | Provide the specs for the fabric at the altars on level 2 and level 5. provide color, brand, width of fabric and patter if any. I sow the owner is purchasing this material. How much extra to they wish to purchase so I can include in my takeoff. |  | We need to finalize the fabrics. However it will be a 54" wide mohair or velvet. No pattern. Will check with owner on attic stock needs. ¦ ¦ When you get the attic stock information from the owner please provide the requirements. Then I will be able to close this item. |  |  | High | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 12/03/2020 |  |  |  |  | Closed | 12/06/2020 | 01/13/2021 | 08/12/2020 | 08/06/2020 | 08/04/2020
634 |  | 0 |  |  | Request for Information | Column Top of Pier Elevation | The 3 columns at gridline AB in the slab on grade area are shown to be bearing on top of a pier which is to terminate at 99'-4". GSW has buit these columns to bear at elevation 98'-4". Is it possible to terminate these piers at 98'-4"? |  | Structurally it is possible to have the columns bear at 98'-4" but several trades may be effected by this decision. This needs to be coordinated with the general contractor please advise on decision that is made. |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 08/05/2020 |  |  |  |  | Closed | 08/12/2020 | 08/10/2020 | 08/06/2020 | 08/05/2020 | 08/05/2020
635 |  | 0 |  |  | Request for Information | East Tower Dry Sprinkler system | The fire protection contractor is installing a dry system for the East Tower there will be an air compressor that needs power and several different switches that need to be monitored by the fire alarm system these are not on our drawings see attached for location of equipment please advise |  | Provide 120v circuit from L3S3 to air compressor, provide fire alarm monitor connections for the pressure switch, flow and tamper switches per manufacturer's instructions for system being installed. Plan changes to be issued as part of upcoming CCD. ¦ See CCD-081 that was issued 9/11/20. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 08/06/2020 |  |  |  |  | Closed | 08/13/2020 | 09/22/2020 | 09/16/2020 | 08/18/2020 | 08/06/2020
636 |  | 0 |  |  | Request for Information | Flat screen rm 042 | EP100 keyed note P4 refers to wall mounted tv in room 042 see markups in attachment. We need mounting height and location of flat screen AE4013 Detail B4 shows a dry erase board in this location. Please Advise. |  | Please provide electrical items (conduit, boxes and power) as noted on sheet EP 100. This is for future use, should there be desire for a wall mounted TV. For now the j-boxes to have cover plates. the dry erase board to be installed as shown on sheet 4013. ¦ Box needs to be 60" high. ¦ EP100 is calling for a specialized box behind the flat screen could you give us an elevation for this box. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 08/06/2020 |  |  |  |  | Closed | 08/13/2020 | 09/08/2020 | 09/01/2020 | 08/07/2020 | 08/06/2020
637 |  | 0 |  |  | Request for Information | AE140 - Annex Basement Dimensions | There are multiple dimensions and wall types missing on AE140 (see attached drawing). Please provide provide dimensions/wall-types. |  |  |  |  | Medium | Aaron Bowers | Pete King Commercial | Westland PE’s |  | 08/06/2020 |  |  |  |  | Closed | 08/13/2020 | 08/10/2020 | 08/10/2020 |  | 08/06/2020
638 |  | 0 |  |  | Request for Information | Dome Ceiling Finish Thickness Inquiry | Currently the ceiling design of Instruction room A-3 (210) and B (211) shows 1-layer of 5/8" gypsum board with a veneer plaster finish (ceiling type C2). The radius for the barreled & dome ceilings is too tight for 5/8" gypsum board. Please advise what size gypsum board will work with the tight radius of these ceilings. Please advise the thickness of the veneer plaster. | Install 2 layers of 1/4" in locations with the tight radius restrictions. | the suggested (2 layers of 1/4" gyp) is acceptable. ¦ the same thickness as the plaster veneer being applied elsewhere. ¦ ¦ What size thickness does the plaster need to be? |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 08/06/2020 |  |  |  |  | Closed | 08/13/2020 | 08/11/2020 | 08/11/2020 | 08/10/2020 | 08/06/2020
639 |  | 0 |  |  | Request for Information | Delete north roof drain solid pipe and correlating RDCO's | Per field conversation with Eric Jamison. The roof drain lines that are marked with pink line are to be deleted. These roof drain connections and clean outs are to be returned to what the original design showed and will be connected to the storm drain line. Please reference the attached drawing for additional information. |  | It would be our recommendation to keep both pipes. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 08/07/2020 |  |  |  |  | Closed | 08/14/2020 | 09/22/2020 | 08/26/2020 | 08/10/2020 | 08/07/2020
640 |  | 0 |  |  | Request for Information | roof drain for lanscaper shed | The roof drain connection for the landscaper shed is shown to connect to the storm drain that has already been installed and is 18 feet deep. Instead of digging that deep to connect to the storm drain system, is it possible to connect the roof drain clean out at the landscaper shed to SDCO #01? |  | This connection can work. I have a bit of hesitancy with it because the line almost does a 180 degrees.. Normally you don't like to bend more than 90 degrees. However, with the low flows and the cleanout available right there. This connection can be made. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 08/07/2020 |  |  |  |  | Closed | 08/14/2020 | 08/13/2020 | 08/13/2020 | 08/10/2020 | 08/07/2020
641 |  | 0 |  |  | Request for Information | Basement Layout | Please see attached sketch noting existing conditions in relation to grids H3 & HD. During our meeting this morning it was noted that the new LVL walls were to be aligned with the existing stone columns (those wrapped with carbon fiber). This represents the columns related to the grids. It appears that the thinnest area occurs at grid HE and that the LVL walls will need to follow this line unless directed otherwise. Please clarify where these walls will align as this will affect our steel in the font level. We have also located the new WF beams supporting level 2 in reference to grids for the LVL walls running north to south along grids HE & HC. Please clarify that the intent along these walls is to match the opening created at level 2. |  | Structurally we take no exception to what is being proposed as long as architect is okay with the layout dimensionaly. ¦ Please refer to ASI 28, 28R.1 and CCD 87R.1 for the new LVL layouts. ¦ If the column on grid line HE is the furthest column inward that will be the control line of where the face of baptistry LVL walls will be placed. Field verify beam lengths and adjust them accordingly. The LVL walls at level 2 shift and are not intended to line up with the lower LVL walls in the baptistry. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 11/12/2020 |  |  |  |  | Closed | 08/14/2020 | 11/16/2020 | 11/13/2020 | 08/10/2020 | 08/07/2020
642 |  | 0 |  |  | Request for Information | Fire protection site supply line. | Related Scope: Civil/Fire suppression Related Documents: C.15/FP100/PS100 Description: Per FP100 note 10 and PS 100 note 2 states to “See civil plans for continuation.” C.15 Fire & life safety plan shows the line supplying the temple, but it has no note indicating that it is to be replaced as a new line. Is it the intended to replace this line? If it is to be replaced to what extant is it to be replaced (ie. From post indicator to building)? Costs are anticipated with this work. Please advise. |  | Replace this line with a 6" PVC C-900 (DR-18) Line. See the 2 attached sheets. ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 08/08/2020 |  |  |  |  | Closed | 08/16/2020 | 09/22/2020 | 08/22/2020 | 08/10/2020 | 08/08/2020
643 |  | 0 |  |  | Request for Information | Historic jacket wall epoxy dowel spacing clarification | The typical jacket wall detail 1/S241 calls out the "#4 hooked dowel at 24" O.C. @ each layer of foundation stone". Does this mean at every horizontal stone transition layer the #4 dowel needs to be installed at 24" spacing or is a horizontal and vertical grid pattern of 24" in both directions acceptable? The way we submitted this in the rebar shops we anticipated 24" grid pattern because the stone sizes/layers vary significantly. Please clarify intent. This issue has arisen from the special inspector. |  | A 24"o.c. grid spacing was intended similar to what was shown in the shop drawings. ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 08/10/2020 |  |  |  |  | Closed | 08/13/2020 | 08/11/2020 | 08/11/2020 | 08/10/2020 | 08/10/2020
644 |  | 0 |  |  | Request for Information | Stair 1 Floor Finish Details | The current detail at stair 1 (Annex) denotes a hardwood tread configuration. The latest floor finishes have changed this finish to carpet on the treads with Hardwood at level 1 and LVT at level 0. Currently there is no detail for carpet at the stairs. Please provide a detail containing substrate information, etc for this condition as well as the carpet to wood transition at level 1. We know the carpet is 3/8" thick, but will need thickness of substrate as well as offset dimensions for tread nosing in order to configure our steel pan system. |  | Transition details can not be provided until a wood floor substrate is submitted. We are waiting on that submittal from GC. ¦ Scott, it sounds like you have come to a resolution regarding this onsite with Ryan and Brett Glassy. Please provide your resolution. |  |  | High | Brett Glassey | Glassey Steel Works | Interior Designer |  | 08/11/2020 |  |  |  |  | Closed | 08/29/2020 | 10/01/2020 | 09/08/2020 | 08/11/2020 | 08/11/2020
645 |  | 0 |  |  | Request for Information | Annex High Entrance Roof Steel | There are 3 columns on the South of the High Entrance Roof Tower that appear in details and in the architect's model to extend without a termination detail. The top of steel elevations are also not apparent for the remainder of the steel in elevations E, F, G on Sheet S107A. Please clarify |  | Please see attached sketch form ARW and the attached entry tower section C2/AE369 and details D3/AE503 and E3/AE503 showing height of parapet and HSS tube steel at railing posts. ¦ See attached sketch for response information. |  |  | High | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 08/11/2020 |  |  |  |  | Closed | 08/20/2020 | 08/25/2020 | 08/24/2020 | 08/17/2020 | 08/11/2020
646 |  | 0 |  |  | Request for Information | Can Location in Ceiling of 3rd Level East Room | Can light layout has the can lights landing in the bottom flange of the I-beam in the ceiling. They can be moved 5 5/8 closer to the wall in RED or 10 1/2" to the center of the room BLUE. The original location is shown in BLACK. Please refer to the attachment for clarification. |  | PLEASE MOVE THE LIGHTS TOWARD THE WEST WALL AND FOLLOW THE INSTRUCTIONS ON THE ATTACHED SHEET FOR LOCATING THE REMAINDER OF THE FIXTURES IN ROOM 318. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Electrical Engineers |  | 08/11/2020 |  |  |  |  | Closed | 08/14/2020 | 08/12/2020 | 08/12/2020 | 08/11/2020 | 08/11/2020
647 |  | 0 | 230000 | M100A | Request for Information | Duct vs. Structural Pier at Basement Historic | See attached M100A drawing depicting conflict with Return Air duct and structural pier located at grid line HB and H4. | Possible solution is to split the 32x44 RA duct into to different segments to reduce overall size. See attached drawing indicating duct shown in PURPLE with dashed lines may be able to fit west of the pier and pick up this RA ducts | See comment from Brian Oswald, VBFA dated 26-August-2020. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 08/11/2020 |  |  |  |  | Closed | 08/18/2020 | 08/26/2020 | 08/26/2020 | 08/11/2020 | 08/11/2020
648 |  | 0 | 230000 | M101, GI201A | Request for Information | Fire Rated assemblies at Level 1 Annex | Drawing M101, Annex Bldg indicates multiple mechanical shafts, elevator shafts and shear walls with mechanical duct penetrations. Drawing GI201A indicates these areas to be 1hr rated assembly at all walls. Please confirm if fire or fire smoke dampers are required at these mechanical duct penetrations. See attached highlighted drawing for clarification. | Clarify if SD or FSD are required at the highlighted locations shown per the attached. | Please see the attached pdf "RFI_648_Fire Rated assemblies at Level 1 Annex_VBFA" and the comment from VBFA dated 03-Sept-2020. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 08/11/2020 |  |  |  |  | Closed | 08/18/2020 | 09/22/2020 | 09/08/2020 | 08/11/2020 | 08/11/2020
649 |  | 0 |  |  | Request for Information | Annex Wall Heights | Please confirm the wall heights in the Annex are to be full as outlined in the attached document. These heights have been derived from the BIM file. We are planning on framing the wall to the deck above with the Drywall coming up to the Elevation that is out lined in the attachment. For clarity the attached drawing has gone through as a submittal already. We just want to make sure everyone is on the same page because this could change some of the mechanical in this area. |  | All framed walls to be framed and drywalled to bottom of deck above. Typical details to frame out duct work penetrations or bracing walls where needed are found on sheets SS09 and SS10. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/12/2020 |  |  |  |  | Closed | 08/14/2020 | 08/12/2020 | 08/12/2020 |  | 08/12/2020
650 |  | 0 |  |  | Request for Information | Area Wells at Annex | Sheet AE100 denotes (2) Area Wells along the East wall of the Annex between grids A3 & A4. There appears to be no information as to how these are capped (assuming grating is needed here for safety). Please clarify what is to be used for these wells. |  | Refer to CCD-084 for added area well grate covers notes and details. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 08/12/2020 |  |  |  |  | Closed | 08/18/2020 | 08/25/2020 | 08/24/2020 | 08/12/2020 | 08/12/2020
651 |  | 0 |  |  | Request for Information | Data Rm. 039 power | EP100/5 shows one circuit powering outlets on each wall is it the intent for this circuit to power all wall mounted equipment except fire alarm in this room? EC501/3 shows the outlets refered to in question 1 mounted 72" to center. Is this correct? |  | Fire alarm and rack mounted equipment is on separate circuits. Three outlets are on a single circuit. If it is determined that additional equipment will be wall mounted and exceed a typical 20A circuit capacity, then additional separate circuit will be required to split up those three outlets. Please confirm in writing after coordinating with security installers if that is the case and a separate circuit will be noted. Yes, mounting height is accurate as noted. It is intended to facilitate power to wall mounted equipment. Outlets to be flush with plywood as noted. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 08/12/2020 |  |  |  |  | Closed | 08/19/2020 | 09/01/2020 | 09/01/2020 | 08/12/2020 | 08/12/2020
652 |  | 0 |  | S104, EL104B | Request for Information | 1” Electrical Lines Ran Through I Beam | After the placement of the I-Beams in the ceiling of the East room on level 3 that we need to penetrate the I-Beams twice to allow for electrical lighting conduits. Please see attachment for clarification. | Allow for 1” penetrations in center 3rd of I-Beam. | It is acceptable to drill the holes at the locations shown in the attachments. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/12/2020 |  |  |  |  | Closed | 08/19/2020 | 08/18/2020 | 08/17/2020 | 08/12/2020 | 08/12/2020
653 |  | 0 |  | P100A | Request for Information | Basement Gravel Base Under Slab | Per discussion on site it has been discussed the option of changing the gravel under the basement slab to 6” in leu of the 24” as called out in the soils report or should we go to 18” needed for plumbing drainage. Please confirm if this is the case. The dewatering lines would be running flat to their drain and won’t have the slope called for in the plans. This may be a nil point but the plumbing lines below 6” will be below the dewatering system. | Install 18" of gravel allowing for the plumbing drainage. | Scott said the suggestion of 18" is approved. ¦ ¦ This is inside the building and would be best handled by the Mechanical Engineers (VBFA). |  |  | Medium | David Adams | Westland Construction, Inc. | Brian Oswald | VBFA INC CONSULTING ENGINEERS | 08/12/2020 |  |  |  |  | Closed | 08/19/2020 | 08/20/2020 | 08/20/2020 | 08/19/2020 | 08/12/2020
654 |  | 0 |  |  | Request for Information | Micro-pile Rod is Short and to the Side | We have a few all threads inside the micro pile that are below the jacket sleeve. Some of the all threads are far side of the sleeve and adding a coupling then extending the rod up is the fix. Adding a coupling is not an option in one location. as discussed on site please confirm we can wield a piece of all thread to a plate and set it inside aligned with the other all thread and grout it in. this way the load should transfer through. | Confirm | Please see attached sketch for extending the micropile. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/13/2020 |  |  |  |  | Closed | 08/16/2020 | 08/18/2020 | 08/17/2020 |  | 08/13/2020
655 |  | 0 |  |  | Request for Information | Fire Protection in Landscaper's Shed | As far as I can tell there is no fire protection in the landscaper’s shed. Should there be fire protection in that little building? |  | See response from Brian Oswald, VBFA dated 28-August-2020 ¦ Sprinklers are not required. |  |  | Medium | Hyrum Ence | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/13/2020 | CCD_66 |  |  |  | Closed | 08/20/2020 | 09/01/2020 | 08/30/2020 |  | 08/13/2020
656 |  | 0 |  | S248 | Request for Information | Interior Column Sequencing | 1. Core/install strong pipe 2. Cut Micro-Piles to fit column structure 3. Install shims under Flat Jacks 4. Install Flat Jacks 5. Install wide flange beam 6. Install C Channel/wield washers 7. Raise Column Assembly so strong pipe is touching the top of the core. 8. Wield washer to C Channel 9. use come-along straps to hold C Channels tight for wielding 10. Wield washer to strong pipe 12. Install pretension rods tighten rods to 100 kips 13. Grout cure time - Anticipate 4 days 14. Transfer load through Flat Jack - Preload Flat Jacks max 75 kips - Monitor for 30 mins for possible setting. 15. Transfer from water to grout. 16. Give grout cure time. 17. Transfer complete 18. Install reinforcing jacket wall. 19. Inspect reinforcing. 20. Form for 2nd jacket wall. 21. Pour second jacket wall, including around the C Channel. 22. Excavate/grade basement 23. Install plumbing/dewatering 24. Install gravel. 25. Place/inspect re-bar. 26. Place concrete slab on grade. |  | This information should be presented in a submittal rather than an RFI. We were expecting this sequencing procedure to be more detailed. Can you please provide more detailed information regarding the following items: 1-When/how will the steel frame be connected to the micro piles? 2- How will the pretension be accomplished in the dwi dag bars inside the strong pipes? i.e. What method will be used to get the pretension? 3-Will the strong pipe be grouted solid during step #13? 4- Please provide more specific details and procedures as to how the load will be transferred through flat jacks. Similar to what Chris Robins spoke about several weeks ago during a meeting between ARW, Westland and the owner. The following are examples of what we would like to see considered. a. How will a max load of 75 kips be determined? b. How will movement of the stone columns be monitored? c. How will initial micro-pile settlement be monitored? d. What grout is going to be used to for permanent placement in the flat jacks? ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/14/2020 |  |  |  |  | Closed | 08/17/2020 | 08/27/2020 | 08/20/2020 | 08/14/2020 | 08/14/2020
657 |  | 0 |  |  | Request for Information | ASI 39 clarification of opening headers | 1)Attached is a section cut from our approved rebar shop drawings that show the header beam extending to the face of the jacket walls. Section A in ASI 39 leads me to believe we only need to have the beam span the length of the stone wall. Either way our rebar ties will work they will just be splice at a different location. If we can follow the ASI direction it would be preferable. Please clarify. 2) The epoxy dowels in the head on ASI 39 section A show #4 bar at 12". Detail 9/S241 shows #3 dowels. Please clarify. We also assume based on previous discussions these dowels are only on the edge of the openings and not at a 12" o.c. pattern if the #4 detail. |  | Please use ASI 39 for the detailing and construction of the headers. Detail 9/S241 is going to be superceeded by the information shown in ASI 39. ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 08/14/2020 |  |  |  |  | Closed | 08/20/2020 | 08/17/2020 | 08/17/2020 | 08/17/2020 | 08/14/2020
658 |  | 0 |  |  | Request for Information | Room 410 Floor box relocation | The floor boxes in room 410 need to be relocated due to floor joist clashes. The floor joists need to be where they are due to can lights being moved out towards walls. Can we either move the floor boxes from 1' - 10" from the wall to 1' - 7", or cut channels in the plaster walls and install them in the walls? See attached drawing for details. |  | We see no issue in shifting the floor boxes closer to the wall as noted with the 1'-7" dimension. Architect to confirm if they prefer this or moving to the walls. ¦ Moving the floor boxes 1'-7" from the wall is acceptable and preferred. ¦ ¦ Please advise if this is acceptable. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 08/17/2020 |  |  |  |  | Closed | 08/24/2020 | 08/24/2020 | 08/21/2020 | 08/20/2020 | 08/17/2020
659 |  | 0 |  |  | Request for Information | Dimensional Lumber Price Increase | Due to the increase (300%) in dimensional lumber costs while the cost of LVLs are staying constant. Would it be acceptable to purchase LVLs as replacements for the dimensional lumber? | Please Confirm | Confirmed by Zach H (ARW) in our OAC today. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/18/2020 |  |  |  |  | Closed | 08/21/2020 | 08/20/2020 | 08/20/2020 | 08/18/2020 | 08/18/2020
660 |  | 0 |  |  | Request for Information | North and west jacket wall tie rod elevations and questions | Please verify the following regarding tie rod locations at the north and west jacket walls (reference details 1,3/S242, 1/S243) 1) Top row of tie rods will be spaced at 24" at elevation 93'-6 1/2" based on detail showing the row 12" below top of interior jacket wall 2) Second row of tie rods will be spaced at 24" at elevation 91'-6 1/2" (2' below top row) 3) Contractor please verify that the 1" tie rod holes will be core drilled after the jacket wall is placed. 1/4" max oversize (reference RFI 69) 4) EOR in RFI 69 we asked to use epoxy grout for the tie rods. In researching options we feel a epoxy resin would be the best product for this application as it could be pumped into the deep rod holes and the viscosity of the epoxy resin would fill voids in the stone. Please verify if acceptable option and we will submit a product for use. |  | 2. Please install according to RFI 69 Where the direction was given to core drill 1/4 “ bigger then the 1” tie rods. ¦ See responses below: 1) We take no exception to this elevation. 2) We take no exception to this elevation. 4) Epoxy resin is a possible acceptable solution. Please submit product information for review. ¦ Please provide a 3rd row of tie rods on the West wall at elevation 89'-6 1/2". |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 09/14/2020 |  |  |  |  | Closed | 08/25/2020 | 09/15/2020 | 09/15/2020 | 08/19/2020 | 08/18/2020
661 |  | 0 |  |  | Request for Information | Reinforcing Requirements for Cooling Tower Housekeeping Pad | If a house keeping pad is desired under the Chiller. Please advise what the reinforcing requirements are for the cooling tower CT-3 housekeeping pad. |  | As a structural engineer, we do not have control over this requirement. Please consult with architect and mechanical engineer if a housekeeping pad is needed for this chiller. If a pad is desired, then it will be reinforced per the typical housekeeping pad detail 4/S211. ¦ Scott confirmed that we do want a pad under these cooling towers to match the rest. OAC today. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/19/2020 |  |  | 500.00 |  | Closed | 08/22/2020 | 08/20/2020 | 08/20/2020 | 08/20/2020 | 08/19/2020
662 |  | 0 |  |  | Request for Information | Ladder at Cooling Tower Enclosure | If housekeeping pad is desired under the Chiller. Should we shift the stairs over to the wall so it will line up with the walkway below? If this is desired, we will follow the 2" free space as outlined in detail C4 on sheet AE509. This will result in additional cost to re-manufacture the guardrails where the guardrails connect to the ladder handrail. |  | Move the pad to the West as needed to clear the stairs. - OAC Meeting |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/19/2020 |  |  | 2500.00 |  | Closed | 08/22/2020 | 08/20/2020 | 08/20/2020 | 08/19/2020 | 08/19/2020
663 |  | 0 |  | AE4305, AE123 | Request for Information | Lower Ceiling in Room 318 | Would it be acceptable to lower the Ceiling in room 318 2" - 1 1/2". This would allow for the Electrical in this ceiling to be installed. | Lower Ceiling | Please see RFI 652 for acceptable hole locations. If drilling new holes in the beams is problematic then it will be acceptable to remove every 3rd 3/4" dia bolt that is attaching the LVL's to the beam webs. These holes can be made larger to accommodate the electrical lines. ¦ See comments below. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/20/2020 |  |  |  |  | Closed | 08/23/2020 | 08/25/2020 | 08/24/2020 |  | 08/20/2020
664 |  | 0 |  |  | Request for Information | Replacement trees for the Mimosa trees | Direction has been given to replace the two Mimosa trees located at the brides photo radius in the south west corner. Provide direction for the replacement trees to use. |  | Response is attached ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 08/20/2020 |  |  |  |  | Closed | 08/27/2020 | 09/22/2020 | 08/20/2020 | 08/20/2020 | 08/20/2020
665 |  | 0 |  |  | Request for Information | CCD 45R4 4" slab reinforcement | Sheet S100A The call out for east tower rooms between grid HA and HB and H4, H2 calls out #4 rebar at 16" o.c. top and bottom each way. Please confirm this is a single mat of rebar not a double mat. |  | Yes. The reinforcing for the 4" slabs is only a single mat. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 08/24/2020 |  |  |  |  | Closed | 08/31/2020 | 08/25/2020 | 08/25/2020 | 08/25/2020 | 08/24/2020
666 |  | 0 | 230000 | M sheets | Request for Information | Transfer Air requirements at Annex | RFI #649 response indicates wall height requirements at Annex level 0 and 1. It appears that due these clarifications, transfer air pathways and ducts could be required in various locations throughout level 0 and 1 of the Annex. | Please have VBFA review level 0 and 1 of the Annex Building and provide location, sizing and quantities of any transfer air ducts required. | See response from Brian Oswald, VBFA dated 28-Aug-2020 ¦ these items have been taken care of in CCD 28R.3 |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 08/24/2020 |  |  |  |  | Closed | 08/31/2020 | 10/01/2020 | 09/22/2020 | 08/31/2020 | 08/24/2020
667 |  | 0 |  |  | Request for Information | New Light Fixture "LT1A" in CCD-069 | Please provide information for the new back-lit light panels referenced in CCD-069, baptistry font room. Catalog number, description, size, etc. Or provide an updated light fixture schedule with this fixture. |  | See attached revised light fixture schedule and lighting cut sheets. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 08/24/2020 |  |  |  |  | Closed | 08/31/2020 | 09/15/2020 | 09/14/2020 | 08/25/2020 | 08/24/2020
668 |  | 0 |  |  | Request for Information | Column Jacket Interface with Mat Slab | 1/S248 calls for the column concrete jacket to be installed first and then the mat slab to be poured into it. Would it be acceptable to pour the mat slab first then pour the column jackets on top of the mat slab. | It is acceptable. | Our intention was not to have the mat slab below the jacket walls to help prevent any unwanted cracking due to differential movement between the jacket walls and the slab. The mat slab could be placed before the jacket walls, but we recommend the slab be blocked out around the column locations large enough to allow the jacket walls to run past as shown in the current structural details. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/25/2020 |  |  |  |  | Closed | 08/28/2020 | 08/25/2020 | 08/25/2020 | 08/25/2020 | 08/25/2020
669 |  | 0 |  |  | Request for Information | Existing Soil Below Stone Columns | Please advise if we are to remove the soil underneath the stone columns once the load has been transferred to the micro-piles and then infill the void with concrete when the column jacket is poured. |  | Per previous discussions there is no compelling reason to remove the soil below the stone columns and the current details in the drawing show it as such. (See detail 1/S249). It was discussed that removing the soil would result in added cost due to labor and materials. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/25/2020 |  |  |  |  | Closed | 09/01/2020 | 08/25/2020 | 08/25/2020 | 08/25/2020 | 08/25/2020
670 |  | 0 |  | FP104 | Request for Information | FP104 VBFA has specified Extended Coverage - NOT FM Approved | On VBFA’s construction document on FP104 it states to use an “Extended Coverage” Sprinkler, which has already been installed, however, FM does NOT approve any EC sprinklers. In some cases the church can give the approval to FM Global, especially in this case due to the historic nature. Or, does VBFA give us the direction to change the sprinklers to standard coverage sprinklers in which case, will require re-piping and more sprinklers for the protected area. |  |  |  |  | High | David Adams | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 08/25/2020 |  |  |  | 8000.00 | Closed | 08/28/2020 | 09/17/2020 |  | 09/16/2020 | 08/25/2020
671 |  | 0 |  |  | Request for Information | 4th Floor GFRG Crown Molding and Drywall Seam | Per RFI 615, there will be new crown molding on the 4th floor north and south walls/ceilings. We are currently framing these ceilings. The ceilings tie into the GFRG covering the curved portion of the GFRG (see attached drawing markup). This creates an issue because we will not be able to install hat channel within the curve to secure the drywall at the seam which will cause cracking in the future. Please advise if it would be acceptable to delete a majority of the curved portion as shown in the markup. |  | Please see the attached mark-up detail. |  |  | High | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 08/26/2020 |  |  |  |  | Closed | 09/03/2020 | 09/02/2020 | 09/01/2020 | 08/26/2020 | 08/26/2020
672 |  | 0 |  |  | Request for Information | Lighting Sheet for CCD-054.4 R3 | Are there any lighting revisions associated with CCD-054.4 R3? With the creation of storage room 012 is there a separate switch/sensor? Revised lighting layout? No lighting sheet or electrical narrative is included with this directive. |  | See attached EL100B. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 08/26/2020 |  |  |  |  | Closed | 09/02/2020 | 09/22/2020 | 09/17/2020 | 08/26/2020 | 08/26/2020
673 |  | 0 |  |  | Request for Information | Level 0.5 Beam and Bent Plate Dimensions | During a coordination meeting today it was noted that there are multiple issues with the dimensions regarding the floor beams at level 0.5. Please see attached sketch for descriptions of the issues. 1. Shifting the opening has caused the angle connection to run off the embeds. Please advise 2. Dimensions do not allow for enough room for dampers. This beam has maxed out the detail dimensions at 18" from center of beam. Moving much further will result in over-running the embeds. Please advise. 3. Embed is misplaced – please provide remedy for connection 4. Angle outlookers are provided and can possibly be in the way of dampers. What is the max spacing possible for them? 5. Dimensions do not allow for enough room for dampers. Moving much further will result in over-running the embeds. Please advise. |  | Please see attached response from ARW on the various connection solutions. ¦ |  |  | High | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 08/27/2020 |  |  |  |  | Closed | 08/30/2020 | 10/01/2020 | 09/30/2020 | 08/27/2020 | 08/27/2020
674 |  | 0 |  | S249 | Request for Information | Hist. West Wall Load Transfer | Please confirm that we are able to transfer the load on the West wall before the jacket wall is installed? In order to achieve this we will: 1. Lengthen out the pipe sleeve to be just short of the flat jacks and shim plates thus minimizing the load impacts on the Needle Beam. 2. Cut the Micro-piles lower on one side then the other to allow for the Pipe Sleeve to pass through. |  | We confirm, except lengthening the pipe sleeve is not necessary. The pipe sleeve is only required in the stone wall, it does not need to protrude out of the stone wall. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 08/28/2020 |  |  |  |  | Closed | 09/03/2020 | 09/01/2020 | 08/29/2020 | 08/28/2020 | 08/28/2020
675 |  | 0 |  |  | Request for Information | RG-4A Grills Level 5 Corridor | On M105 in the North and South Corridors, there are (2) Return Grill callouts. One is a RG-3A 10" ROUND and the other is a RG-4A 8" ROUND. According to the schedule on M603 an RG-3A is a 20"x 20" and a RG-4A is a 12"x 12" is this correct or should they all be a RG-4A so they match aesthetically? Also if the RG-3A grills change to a RG-4A is the quantity correct or will an extra grill be required in each corridor? Please advise. See attached clouded drawings for clarification. |  | See response from Brian Oswald, VBFA on 11-Sept-2020 |  |  | High | Cobe Holmstead | US Mechanical LLC | Mechanical Engineers |  | 08/28/2020 |  |  |  |  | Closed | 08/31/2020 | 10/01/2020 | 09/12/2020 | 08/28/2020 | 08/28/2020
676 |  | 0 |  |  | Request for Information | Clarifications to RCP Layout ASI 10 | Per discussions between CRSA and Jason on 8-27-2020. Please confirm the corridor RCP layouts on levels 5 and 3 are to be per the attached notations to ASI 10. |  | The ceiling layouts on the attachment are outdated. Please refer to CCD-019 showing the medallions being omitted. CRSA has reviewed and confirmed the mock-up ceilings on-site along with centering the pendant lighting with the doors. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/28/2020 |  |  |  |  | Closed | 09/04/2020 | 09/15/2020 | 09/08/2020 | 08/28/2020 | 08/28/2020
677 |  | 0 |  |  | Request for Information | Roof Drains at East Historic Spiral Stairs | Per a conversation between VBFA, Jason, and US Mechanical on 8-27-2020. Refence attached sheet P110A. Please confirm it is acceptable to slope the 4” roof drain line from the north spiral staircase toward the south spiral staircase at the at 1/16” per foot. The routing would be per the original layout of P110A. Please confirm. |  | See response from VBFA. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 08/28/2020 |  |  |  |  | Closed | 09/04/2020 | 09/15/2020 | 09/08/2020 | 09/01/2020 | 08/28/2020
678 |  | 0 |  | S101 / AE100 | Request for Information | Missing Laundry Drop Slab Openings | The openings in the suspended slab for the laundry to fall through from the dressing rooms down to the laundry drop rooms are missing in both the Brother's and Sister's dressing rooms. How would you like them to look? Since they need to be cut into the existing suspended slab, how do we need to handle that structurally? |  | Please provide a angle frame around the outside perimeter of the laundry drops per detail 12/S202. ¦ ARW, Refer to Architectural sheets AE4007 and AE523 for sections and details of the clothing drops. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Structural Engineers |  | 08/28/2020 |  |  |  |  | Closed | 09/04/2020 | 09/18/2020 | 09/17/2020 | 09/09/2020 | 08/28/2020
679 |  | 0 |  |  | Request for Information | RE: CCD_54.4 - Wall Insulation Around the Training Room | On the conformed set of drawings, the concrete wall on AE100 column line A7 has metal studs/furring. It is a wall type 13 & 09, which is an insulated wall. On CCD_54.4, the furring has been removed, thus removing the insulation. My concern is the new walls around the training room. These walls are type 32, which does not get insulation. Wall type 32 is used throughout the project. However, because its a training room, I’m thinking they should be insulated. If so, then the removing of the insulation at the concrete wall, and adding insulation around the training room would be a wash. Please advise |  | Yes, Please insulate north and west walls of the training room (wall type 32). |  |  | Medium | Gary Tonks | Tonks Insulation, Inc. | CRSA ARCHITECTURE |  | 08/28/2020 |  |  |  |  | Closed | 09/04/2020 | 09/15/2020 | 09/09/2020 |  | 08/28/2020
680 |  | 0 | 230000 | M101 | Request for Information | Annex above ceiling duct clashes | Drawing M101. Currently, modeling of the MEP systems within the overall Annex building model is indicating various locations where overhead HVAC duct is clashing with walls above ceiling. See attached drawing for clarification of these three locations. | Please advise if the walls at these clash locations could be lowered to accommodate the HVAC duct. | Lowering the walls below the ductwork in the areas shown is acceptable. Lowered walls need to continue a min. 6" above ceiling and braced to floor frame above per structural recommendations. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 08/31/2020 |  |  |  |  | Closed | 09/07/2020 | 09/15/2020 | 09/09/2020 | 09/01/2020 | 08/31/2020
681 |  | 0 |  |  | Request for Information | Historic Pews | Can we get a finalized pew layout for the 4th floor assembly hall with the new pews and the reused pews labeled? There was discussion about possibly needing to anchor the pews to each other to make sections longer than the 12'4" we will need to know that before we attach the legs. We also need to know if these will be anchored to the floor or free-standing. |  | See comment and Attached drawing dated 9/8/20. Please provide recommended attachment for review. |  |  | Medium | Gary Ramos | AW Carter LLC | CRSA ARCHITECTURE |  | 09/01/2020 |  |  |  |  | Closed | 09/08/2020 | 09/22/2020 | 09/16/2020 | 09/01/2020 | 09/01/2020
682 |  | 0 |  | EL104A, EL104B | Request for Information | Room 408 LV switch relocation, Room 410 switch removal | Due to the installation of finish trim, the LV switches on the east end of room 408 on either side of the East Pulpits are not able to be installed as shown. Also, there is a switch shown in room 410 (GA lounge) at the top of the short staircase on the West side of the room. This is not actually an entrance/exit into this room, and installation in this location would be inordinately difficult. | Move the LV switches on the east end of room 408 to the other sides of the doors as shown on attached drawing. Remove the LV switch above short staircase landing in room 410 from the plans as shown on the same drawing. | The proposed changes are acceptable. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 09/01/2020 |  |  |  |  | Closed | 09/08/2020 | 09/22/2020 | 09/17/2020 | 09/02/2020 | 09/01/2020
683 |  | 0 |  |  | Request for Information | Lighting under Font witness stand | There is a question on how to install lighting under the Baptistry Font Witness Stand. The information we have so far indicates that the underside where the lighting will be installed is open and not conducive to installing recessed can lighting. | There needs to be some sort of enclosed box incorporated into the structure to install the can light into, or we could install LED tape lighting that could conform to the shape of the structure. See attachment for further clarification and LED tape light possibilities. | In the attached update drawing please go to page 5 of 13 detail C. It sows the install of a 1/8" Removable Bronze Soffit Panel |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Westland PE’s |  | 09/01/2020 |  |  |  |  | Closed | 09/08/2020 | 09/02/2020 | 09/02/2020 |  | 09/01/2020
684 |  | 0 |  |  | Request for Information | PIV (post indicator valve) | Drawing C.15 is calling for a PIV and referanced in a detail on drawing C.13 asking for it to be monitored by the fire alarm panel. The EY drawings do not refrence a PIV anywhere Please advise see attachments |  | Provide the monitor module(s) as required back to fire alarm panel. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 09/02/2020 |  |  |  |  | Closed | 09/09/2020 | 09/22/2020 | 09/18/2020 | 09/04/2020 | 09/02/2020
685 |  | 0 |  |  | Request for Information | Channel Interfering with Angle | Upon further investigation we noticed the angle called out to support the wide flange beam is interfering with 2 bolts installed in the saddle. We have attached some pictures for reference. | Install Angle under the wide flange and use shims to get the wide flange beam to the correct height. | Brent White confirmed on site with Dion and Dave that this was an acceptable solution. ¦ Brent, This is the attachment I talked to you about in the basement. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/04/2020 |  |  |  |  | Closed | 09/05/2020 | 09/08/2020 | 09/08/2020 | 09/04/2020 | 09/02/2020
686 |  | 0 |  |  | Request for Information | 4th Floor Crown Molding Tying to Flat Ceiling | While doing the layout for the North and South ceilings on level 4 it was discovered that the inner crown moldings on the wings very in height. I have attached some photos for review showing the variances in elevation from the new ceiling (Flat) to the Existing Crown Molding (Varies). | Match the new ceiling elevation to the existing crown molding. | Yes, match the new ceiling to the existing crown molding to keep same reveal. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 09/02/2020 |  |  |  |  | Closed | 09/09/2020 | 09/11/2020 | 09/08/2020 | 09/03/2020 | 09/02/2020
687 |  | 0 |  |  | Request for Information | 5Th Floor Lighting Hallway 516, 520 and 4Th floor Priesthood | Due to multiple building restraints IE. duct work, framing, j-boxes, mech. and sprinkler piping. We are asking for an exception to use MC to supply lighting in the 5th floor hallway 516,520 and 4th floor North and South side of priesthood room we would run .75 EMT home runs to a J-Box located at access doors and then MC from there. This will also allow future side to side and height adjustment. |  | Locations noted are acceptable. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 09/03/2020 |  |  |  |  | Closed | 09/20/2020 | 09/17/2020 | 09/17/2020 | 09/03/2020 | 09/03/2020
688 |  | 0 |  |  | Request for Information | Skylight Framing | Skylight framing seems to require the curb to be directly mounted to the steel beams. There is not a specific structural detail for the openings as it relates to the ability to have decking bear on the beams as well. Please provide direction. |  | See attached for possible solution. |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 09/03/2020 |  |  |  |  | Closed | 09/10/2020 | 09/15/2020 | 09/08/2020 | 09/08/2020 | 09/03/2020
689 |  | 0 |  |  | Request for Information | Roof Frames smaller than 18" | GSW is utilizing detail 17/S201 (attached) for all roof openings greater than 18", but we are unable to locate a detail for opening smaller than 18". Please provide direction if members are required for these openings (ie: roof drain frames, etc). |  | Please see detail 14/S202. |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 09/08/2020 |  |  |  |  | Closed | 09/14/2020 | 09/15/2020 | 09/08/2020 | 09/08/2020 | 09/08/2020
690 |  | 0 | 230000 | M100A | Request for Information | CCD 49R2 Duct Routing conflict | Following review of CCD#049R2 and the indicated routing of the duct work as shown, the duct has been implemented into the BIM model and is showing conflicts in various locations. See attached marked up drawing for your review and response. | Following review of the attached proposed duct sizing and routing to CCD#049R2, please advise if these changes to sizing and routing are acceptable. | Please see comment from Brian Oswald (VBFA) dated 15-Sept-2020 |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 09/09/2020 |  |  |  |  | Closed | 09/13/2020 | 09/15/2020 | 09/15/2020 | 09/10/2020 | 09/09/2020
691 |  | 0 |  | AE4007 | Request for Information | Added casework Laundry Rm 028 | Submittal 064023.07.00, Fetzers submittal #3 drw 409.1, Architect added 3 ea. tall cabinets to the laundry room. Will this change be coming forth in a CCD or is Fetzers to submit pricing to the GC based off the redline comments? |  | See CCD 054.4r5, Sheet AE4007 shows updated cabinetry in Laundry Room ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 09/09/2020 |  |  |  |  | Closed | 09/16/2020 | 11/09/2020 | 11/02/2020 | 09/10/2020 | 09/09/2020
692 |  | 0 |  |  | Request for Information | Redline door schedule/ door jambs questions | Questions from submittal 064023.02.00, Fetzers submittal # 1 drw. 310.1 1. Door 125A is metal door, not in Fetzers scope 2. Door 147B glass transom should be insulated glass. All transoms on exterior doors should be insulated 3. Door 191 and 194 are metal doors 4. Doors 191, 193, 193B, 194, 195, indicate where these doors are located. Do not see these doors on the floor plan. 5. Door 184C Hardware schedule or drawings do not indicate an astragal between double doors. Clarify if this astragal will be wood or metal. This same comment for all double doors. Is astragal needed and will the astragal be wood or metal? |  | 1. Correct a. Door 125D has been changed to Hollow Metal (See CCD 101) 2. Yes, Insulated glass transoms at all exterior doors 3. Door 191 – Hollow Metal Door and Frame at Gardener Restroom Door 194 – Hollow Metal Door and Frame at Grounds Keeper Storage 4. Door 191 – Hollow Metal Door and Frame at Gardener Restroom Door 193 – Dumpster Gate, Use Existing Door 193B – Dumpster Gate, Use Existing Door 194 – Hollow metal Door and Frame at Grounds Keeper Storage Door 195 – Metal Gate into Cooling Towers, Use Existing 5. Door 184C - On a temple, I would only use an astragal if the door was rated. The doors should be in the correct tolerances (1/8” at the meeting edge of the pairs). I have used a surface mounted astragal at back of house exterior doors 194, 034, and 034A. A set of meeting stile astragals has been used on door 030. If an astragal other than the meeting stile astragal is used, the door needs to be coordinated to close correctly. I don’t believe the added hardware is something the Owner will want to entertain. There may have been some wood astragals used on the historic doors? If so, and if the Owner feels there is a need for the astragal, then we should look at this opening x opening and make a determination. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 09/10/2020 |  |  |  |  | Closed | 09/17/2020 | 12/17/2020 | 12/11/2020 | 09/10/2020 | 09/10/2020
693 |  | 0 |  |  | Request for Information | Brides Exit Door 147B | Brides exit door 147B calls for a jamb head with panel trim D1/AE631. Depth of the jamb is wall type 74 which is 14 ¼”. By the time you build the outside bevel in the wall the jamb is aprox. 7 ½” deep. The jamb is not wide enough for a panel jamb. The jamb should be a simple jamb, no panel and trim. Please clarify the details of this door jamb. |  | Proceed with Simple Jamb. Details similar to E1/AE633, with the exception the interior casing will be flush will the wall (similar to E2/AE633) ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 09/11/2020 |  |  |  |  | Closed | 09/18/2020 | 12/10/2020 | 12/10/2020 | 09/14/2020 | 09/11/2020
694 |  | 0 |  |  | Request for Information | 5th East Tower Ceiling Beams | We have been working on the new plan for beefing up the tower. The wall picture shows where the beams go in relation to the mechanical cut outs that are laid out, we only have 10” of space from bottom of Beam. On the two outside beams we will not have solid wall underneath it to carry the load of the beam and tower. The other factor is that the duct cutout rises 4 inches a foot which allows for even less pillow block. Please let us know what you think and how we should proceed. |  | This has been discussed with Josh Nay through email and conference calls. The pillow block for the beams and the concrete for the mechanical openings will be poured together and built integral rather than separate. Please get with Josh for more detailed information if needed. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/15/2020 |  |  |  |  | Closed | 09/19/2020 | 09/23/2020 | 09/23/2020 | 09/15/2020 | 09/15/2020
695 |  | 0 |  |  | Request for Information | CCD 089 New fireline connection point | On CCD 089, it shows the new 6" fireline is to be connected to the 8" mainline in 200 E. The existing fireline is 6" so can the connection for the new replacement line be made at the location of the post indicator valve instead of in the road? If we have to replace the section from the post indicator valve to the 8" mainline it also would involve the fire hydrant and culinary water connections as well as a lot of restoration of asphalt, concrete, fence, traffic control, encroachment permits, ect. Please advise. |  | Yes the 6" fireline can start from the post indicator valve. |  |  | Medium | Clint Foster | Sunroc Corporation | Civil Engineers |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 09/22/2020 | 09/16/2020 | 09/16/2020 | 09/16/2020
696 |  | 0 |  |  | Request for Information | Cored holes existing foundation wall at grid AH | Attached is proposed locations of 6-4" holes thru foundation wall at grid AH 8' north of A2 (holes are for electrical feeder conduits) |  | Please locate the existing rebar in the wall and core the holes where they miss the rebar. Please keep holes no closer than 6" to the adjacent hole. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 09/16/2020 |  |  |  |  | Closed | 09/19/2020 | 09/23/2020 | 09/23/2020 | 09/17/2020 | 09/16/2020
697 |  | 0 | 250000 | MI 105 | Request for Information | T-stat locations at Historic Level 5 | Fifth Level Hallway 520 shows the T-stat for V 5-09 at the West end mounted flush in a Solid Sandstone Block Wall that appears to not include furring. We would like to move it to the perpendicular wall that is to the North, and place it flush in the wall 12" out from the corner. This is a framed plaster wall and can accept the Stat Location without the removal of sandstone structure. It moves the T-Stat away from the supply vent (this eliminates false readings). It remains on an interior wall in the area being conditioned. The elevation of that wall shows no obstructions. Its placement would be to the left of the access door serving level 4 ceiling and to the right of the West end sandstone wall near grid HF and H2. | Please advise if this t-stat relocation is acceptable. | Please see comment from Brian Oswald (VBFA) on 18-Sept-2020 |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 09/22/2020 | 09/18/2020 | 09/16/2020 | 09/16/2020
698 |  | 0 | 250000 | MI 105 | Request for Information | T-stat location at Historic Level 5, serving V 5-04 | Fifth Level Hallway 516 shows the T-stat for V 5-04 at the West end mounted flush in a Solid Sandstone Block Wall that appears to not include furring. We would like to move it to the perpendicular wall that is to the South and place it flush in the wall 12" out from the corner. This is a framed plaster wall and can accept the Stat Location without the removal of sandstone structure. It moves the T-Stat away from the supply vent (this eliminates false readings). It remains on an interior wall in the area being conditioned. The elevation of that wall shows no obstructions. Its placement would be to the right of the access door for level 4 ceiling and to the left of the West end sandstone wall near grid lines HF and H4. | Please advise if this t-stat relocation will be allowed. | Please see comment from Brian Oswald (VBFA) on 18-Sept-2020 ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 09/22/2020 | 09/18/2020 | 09/16/2020 | 09/16/2020
699 |  | 0 | 250000 | CCD#038 Revisions | Request for Information | T-stat locations at Historic Level 5 stairwells | CCD 38 added T-Stats in Stairwells S-7 and S-6 on the fifth level are shown on Solid Sandstone Block Walls that appear to receive no furring. If we move them 24" further into the stairwells we would be able to flush them in the pipe chase that goes between the 5th and 4th levels. This would allow the placement of the T-Stat without the removal of Sandstone Structure. | Please advise if these t-stat relocations are acceptable. | See comment from Brian Oswald (VBFA) on 18-Sept-2020 |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 09/22/2020 | 09/18/2020 | 09/16/2020 | 09/16/2020
700 |  | 0 |  |  | Request for Information | Visitor center roof drain | During the subgrading around the visitors center the roof drain was exposed. The current roof drain elevation is 8" below the stucco. This will interfere with the landscaping work around the visitors center. Please advise. |  | Per direction from Chris Robbins, this is a civil/landscape issue. No work is to be done inside the visitor center. ¦ The attached drawing shows bringing the roof drains from the visitor's center into #10-SDMH. Cap off the existing roof drain pipes where they are detached to prevent a backflow of water. ¦ ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Clint Foster | Sunroc Corporation | 10/08/2020 |  |  |  |  | Closed | 09/27/2020 | 10/19/2020 | 10/08/2020 | 10/12/2020 | 09/16/2020
701 |  | 0 |  |  | Request for Information | Dock Dimension Clarifications | While laying out the dock, the south wall of the existing dock was found to be 4 to 5 inches to far to the North. The elevation of the dock floor is also approximately 1 1/2 to 2 inches low of elevation 100. It is proposed that we thicken the south wall of the dock the needed amount which would require a detail of required rebar and information to attach to the existing wall. (See attached sketch). It is also proposed to use a self leveling concrete mix (Rapid Set) to bring the existing dock up to elevation 100. (See attached material info) |  | Please see CCD87-0R.1 for details on thickening the concrete walls around the dock. Also, in review of the Concrete Leveler product by Rapid Set, it appears that this particular product is not intended to be used as the finished floor surface so we advise against using this. We would recommend using TRU Self-Leveling by Rapid Set instead. This particular product is meant to be the finished surface. See attached for the data sheet on this application. ¦ See CCD-087 thru CCD-087R.3 along with comments below from ARW. Also see the TRU self-leveling product data sheet attached from ARW to be used. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 10/28/2020 | 10/21/2020 |  | 09/16/2020
702 |  | 0 |  | B1/AE 630 | Request for Information | AV cut out at doors 209 210 208 | Provide the cut out sizes of the holes for the AV projector lens in the transom, room side of door 208, 209, 210. In previous temples this has been 6". Please verify the AV equipment will fit with the location of these holes as shown. Detail B1/ AE 630 shows the camera lens to be at a slightly different position that the location of the cut our in the transom. |  | Only one projector per room as directed by Brad Justensen (Owner's AV rep). 6" hole centered in transom and between decorative muntins. See attached PDF's ¦ ¦ CRSA will need to review and reply to this RFI regarding architectural details. Envision AV can assist with coordination with Brad Justensen with Owner AV group if needed for any questions. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 09/16/2020 |  |  |  |  | Closed | 09/23/2020 | 12/17/2020 | 12/16/2020 | 09/24/2020 | 09/16/2020
703 |  | 0 |  |  | Request for Information | Jacket wall slope slab dowels | On sheet S100A there is a section cut on the east wall referencing 4/S247. On this detail there is a #4 dowel that is shown at 12" o.c. tying into the jacket wall from the slope slab. On the same detail it says to reference detail 5/S249 which does not show this dowel. The other typical sloped slab details 4/S249, 1/S243, 1/S241 are similar to 5/S249. Please verify if the #4 dowel is needed at the location shown on detail 4/S247. With the way the jacket walls are being formed it was our understanding this was not needed based on the other details. If the dowel is needed on the east wall as shown it will need to be drilled and epoxied later. |  | Please provide the #4 dowels per detail 4/S247. It is acceptable to drill and epoxy the dowels in after the wall is constructed. Please use 6" embedment for the dowels. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 09/17/2020 |  |  |  |  | Closed | 09/24/2020 | 09/23/2020 | 09/23/2020 | 09/17/2020 | 09/17/2020
704 |  | 0 |  |  | Request for Information | Wall mounted electrical devices | A. Confirming that as per. Scott Gilberg and Jason Fullmer discussion 9/16/2020 we are to proceed forward overlaying electrical and furniture drawings to determine the best location for devices, if no furniture is present scale drawings with blue beam. B. We request a typical detail providing location of switches,outlets, thermostats, speaker strobe,and etc. from edge of door rough opening. Please confirm |  |  |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 09/17/2020 |  |  |  |  | Closed | 10/08/2020 |  |  | 09/17/2020 | 09/17/2020
705 |  | 1 |  |  | Request for Information | East confirmation room 063 jacket wall | Please confirm that the adjustments shown in the attachment are the ones we talked about 09-23-2020. They are in the middle of forming this up so a quick response would be appreciated. |  | Confirmed |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 09/23/2020 |  |  |  |  | Closed | 09/21/2020 | 09/23/2020 | 09/23/2020 |  | 09/23/2020
706 |  | 0 |  |  | Request for Information | Angle Iron Over Doors | We have core drilled for the C Channel and on the West historic wall. That is when we realized the Interior portion of the C Channel is interfering with the Joist for the Floor above. This is occurring at the 2nd and the 3rd floors please see the attached pictures for reference. This condition was worked through on site and it was decided that an Angle Iron can be used to help support the stone in place. The size for the Angle Iron is 6”x6”x3/8” with holes drilled to match the C Channel. This will be installed with the same through bolts as the C Channel with 4”X4”X1/4” plate washers. | Confirm the above for install. | This is acceptable and was addressed in ARW's construction observation report #29, item 29-2. Please see this report for additional information. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/18/2020 |  |  |  |  | Closed | 09/21/2020 | 09/23/2020 | 09/23/2020 | 09/18/2020 | 09/18/2020
707 |  | 0 |  |  | Request for Information | Font wall coordination questions | 1) Attached are the formwork plans for the radius font walls. They have been coordinated with Historical Arts dimension plans. Please confirm architecturally these will work? 2) During onsite coordination it was discovered that the CC3 columns will need to be extended 8" in order for the embeds to fit. We have not seen this adjusted on the structural plans. Please confirm this is correct? (See S100A and attached Glassey embed drawing EP12) 3) Due to the tight tolerances and forming limitations with the radius walls and what Historical Arts will require for the font we would like to propose that the CC3 columns be poured after the concrete radius walls. See attached sketch of proposed method and verify if this will work with post installed dowel epoxied with 6" embedment for the CC3 column? |  | CRSA has verified dimensions with HACI plans. See CCD 097 - Access under Font, for locations of blockouts in both radius foundation walls and added CW-2 walls. ¦ ¦ ARW Response: 1) Please verify with architect 2) It is acceptable to extend the CC3 column as shown. 3) It is acceptable to pour the CC3 column after the radius wall and dowel into radius wall as shown in the provided attachment. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 09/21/2020 |  |  |  |  | Closed | 09/28/2020 | 11/03/2020 | 11/02/2020 | 09/23/2020 | 09/21/2020
708 |  | 0 |  |  | Request for Information | 4th Floor Vestibule 409 and 411 lighting | The recessed cans in both of these areas go thru LCP-T3 we would like to relocate them to LCP-T5 as recommended by our lighting control vendor. See attachment |  | Envision approves this recommendation. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 09/22/2020 |  |  |  |  | Closed | 09/29/2020 | 09/22/2020 | 09/22/2020 | 09/22/2020 | 09/22/2020
709 |  | 0 |  |  | Request for Information | East Tower Lighting at all Levels | Due to multiple building restraints IE. duct work, Framing, J-Boxes, Mech. and Sprinkler piping we are asking for an exception to use MC. to supply lighting at all rooms of the east tower floors 2-5 circular stairs, center room and vestibules. MC from can to can not to exceed 15' we would run .75 EMT conduit home runs to j boxes in accessible areas and then MC from there. This will also allow future side to side and height adjustment . |  | Acceptable as noted. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 09/22/2020 |  |  |  |  | Closed | 09/25/2020 | 10/01/2020 | 09/24/2020 | 09/22/2020 | 09/22/2020
710 |  | 0 |  |  | Request for Information | ADA Restroom Stall Layout | Reference sheets P401, P402, AE100, AE101. At restrooms 027, 028, and 134 the ADA water closet WC-1 is shown close to the toilet partition with the grab bar mounted to the toilet partition. See attached. Would it be acceptable to move the WC-1 toward the framed wall and mount the grab bar to the wall? |  |  |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 09/22/2020 |  |  |  |  | Closed | 09/25/2020 | 10/19/2020 |  | 09/22/2020 | 09/22/2020
711 |  | 0 |  |  | Request for Information | Reinforcing Steel at Remaining Suspended Floors | Westland proposes to install a rebar mat in the suspended floor at the Baptistry Level 0.5 AND Hall 190 AND Hall 145 & 146 - #3 at 12” or 16” on center. Please advise. |  | This is acceptable. If reinforcing is desired, then we recommend #3 bar @ 12"o.c. pattern for the reinforcing. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/22/2020 |  |  |  |  | Closed | 09/29/2020 | 09/23/2020 | 09/23/2020 | 09/22/2020 | 09/22/2020
712 |  | 0 |  | A2/AE4109 | Request for Information | Door 115A | Current door schedule cased opening 115A calls for door type 8, with a 4’ opening. This was change to match the other radius jambs in the family file and administration area. Originally this door was and type 11 ellipse shape jamb. If we make this a type 8 and a 4’ opening the top of the casing will be 120”. Current ceiling height is 120” and there is a 6” crown molding in this room. See attached sketches. Provide direction for this opening | Suggestion: make the opening to the work space 36” or leave the casing a ellipse shape as previously design. | We are going to keep this opening as Type 12 (elliptical). Updated Door schedule in CCD 101r1 ¦ Please see CCD 101R.1 that was issued back in 01-04-21 showing this changing to door type 12. ¦ ¦ We will close this when we receive CCD 101 R1 |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 09/23/2020 |  |  |  |  | Closed | 09/29/2020 | 02/09/2021 | 02/05/2021 | 09/23/2020 | 09/23/2020
713 |  | 0 | 265600 |  | Request for Information | Exterior Light Poles | Quantum lighting originally had these poles in their package, but was told they needed to pull this out and have Rocky Mountain Lighting (RMLC) provide them to match existing poles. We just received correspondence that RMLC will not be able to meet the specs as per Envision Engineering. For additional information please see the attached document. |  | see comments from David Tibbitts dated 9-24-2020 |  |  | High | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 09/24/2020 |  |  |  |  | Closed | 09/27/2020 | 10/01/2020 | 09/24/2020 | 09/24/2020 | 09/24/2020
714 |  | 0 |  | AE101 | Request for Information | Admin 113 Wall Thickness Changes | In CCD_62 the West wall of Administration 113 doubled in thickness. This change wasn't clouded so we are not sure if it was intentional or not. I believe it was intentional because it would make all the cased openings in that room the same thickness. Please see the attachment and advise. | Advise whether we should price this as part of CCD_62 or if this will be released officially in a future CCD. OR Provide direction to omit the change. | Please see CCD-062R.1 showing the clouded wall type/thickness change that should of been included in the previous CCD-062. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 09/25/2020 |  |  |  |  | Closed | 10/02/2020 | 10/28/2020 | 10/20/2020 |  | 09/25/2020
715 |  | 0 |  |  | Request for Information | Rebar Layout 0.5 Level | Please confirm that we are to order and install the rebar in accordance with the attached plan. |  | The attached plan is an acceptable solution to the slab reinforcing for the Level 0.5 slab. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/29/2020 |  |  |  |  | Closed | 10/02/2020 | 09/30/2020 | 09/30/2020 |  | 09/29/2020
716 |  | 0 |  |  | Request for Information | Pile Cap Stitch Weld Confirmation | Please confirm the following; “The pile cap needs to be stitch welded to the pile sleeves with a 2” long x ¼” fillet weld all around the sleeve. Any shim plates should be attached to the pile cap with 2” of ¼” weld on all 4 sides of the shim plate.” The above was taken from an email Sent 9/28/2020 between Zach, Creg, Dion, Josh and David. For reference I have attached the email to this RFI. |  | Confirm ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 09/29/2020 |  |  |  |  | Closed | 10/02/2020 | 09/30/2020 | 09/30/2020 | 09/29/2020 | 09/29/2020
717 |  | 0 |  |  | Request for Information | Casework detail Grab and Go | See attached sketch. Provide details of casework below computer screen. Provide cross section of cabinets. Are there drawers or false drawer fronts. What is depth of cabinet and height |  | Please see CCD-054.4R.4 for Added dimensions and detail callouts. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 10/28/2020 |  |  |  |  | Closed | 10/07/2020 | 11/13/2020 | 10/23/2020 | 09/30/2020 | 09/30/2020
718 |  | 0 |  |  | Request for Information | Metal site fence | This is a confirming RFI due to a field conversation with Chris Robbins that the site fence material can be salvaged and reused. The fence material is to be labeled or tagged for tracking. The old fence is to be stripped of old paint, fix any flaws, and primed. It needs to be in good shape similar to the new fence that is to be provided. |  | This is correct, fence material will salvaged, stripped, repaired and painted to the same quality and the new fence sections that will be installed. Both old and new fence material will be painted with "Quaker Bronze" Sherwin Williams paint as shown on the mockups. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 09/30/2020 |  |  |  |  | Closed | 10/07/2020 | 10/13/2020 | 10/08/2020 | 09/30/2020 | 09/30/2020
719 |  | 0 |  |  | Request for Information | CCD 077 Fountain Basin | In the fountain basin CCD 077 changes the grid at the false floor to Duragrid cut into 18” x 18” squares with the 2 x 2 tile adhered. Are all of the grids expected to be removable for fountain maintenance or will there be a certain amount removable? Please clarify details here. |  | All of the 18"x18" grids are desired to be removable to provide access to maintain the fountain. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 10/02/2020 |  |  |  |  | Closed | 10/09/2020 | 10/28/2020 | 10/23/2020 |  | 10/02/2020
721 |  | 0 |  |  | Request for Information | Elevator 5 footing and pit wall coordination | In RFI 247 we anticipated the elevator pit to be at elevation 87' per the response. In CCD 62 sheet AE337 the pit elevation has been changed. In order to make the CW2 pit walls work we are proposing that a FC-2.0 footing be placed below the baptistery mat footing at elevation 86' (top of footing) and the CW2 walls placed above. This proposed method will also allow the continuation of the north and east jacket walls and retain the soil/concrete at the pit slab. See attached sketches of the sequence that we are proposing. Please confirm this will work and confirm the proposed elevations are acceptable? |  | Based on a conversation between the design team and Westland Construction, it is noted and determined that the elevator pit will be 5feet deep and will be constructed similar to what is shown in the attached drawing. These modifications to the elevator pit will be made to details 3/S246 and 8/S241 in a forthcoming CCD 87-R.2. ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 10/05/2020 |  |  |  |  | Closed | 10/12/2020 | 10/06/2020 | 10/06/2020 | 10/05/2020 | 10/05/2020
722 |  | 0 |  | EL102B | Request for Information | 2nd floor spiral staircase Exit Signage Locations | The current location of the Exit Signs on the 2nd floor in the spiral staircases (S-6-2, S-7-2 into vestibules 221, 220) place the Exit Signs where they would be difficult to see. These Exit Signs are in the path of the planned Emergency Evacuation Plan according to Ray Anderson (St. George Temple Head of Security) which makes them especially critical. | It is proposed that we relocate the Exit Signs to the sides of the doorways at 8' above finished floor to center. They would be placed on the side of the door closest to the stairs going up where most of the evacuating people would be coming from. Also it is proposed that the installed Exit Signs be the Wall Surface Mount style to accommodate installation on the curved surface of the spiral staircase walls. | The general location shown is acceptable; however, the exact location needs to be coordinated in the field to make sure that it meets the visibility requirements in all National, State and Local Codes. After this is done the Architect will need to provide the exact dimensional location. ¦ Move the exit signs to the proposed locations beside the doors at 8'-0" A.F.F. and 8" from Edge of sign to edge of the scheduled door casework. ¦ ¦ Please coordinate and provide the exact locations for the exit signs |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 10/05/2020 |  |  |  |  | Closed | 10/12/2020 | 11/16/2020 | 11/13/2020 | 10/20/2020 | 10/05/2020
723 |  | 0 |  |  | Request for Information | New Sleeve for Tower Dome penetration for Dome Ext. Lighting | The current sleeves that penetrate the dome from inside to outside (8 times) present at least 3 problems: 1- They currently leak. 2- They don't allow for sealing around the SJ cord. 3- They present a trip hazard on the standing/walking platform inside of the dome. | We propose that the old sleeves (8) feeding the dome exterior lighting be removed and replaced with different sleeves as shown in the attached details. The new penetrations would be sealed. Is there a sealant that is recommended to be used? If not, we would use Sika PRO SELECT polyurethane construction sealant which we have used effectively in the past. It is paintable. | David, The proposed Penetration Detail appears well thought out and if executed properly should completely seal the openings; however, it is not clear if the existing dome openings will be reused, or if new openings are being proposed. If new openings are being proposed how will the existing opens be sealed. Please clarify. Thank you, David Tibbitts Senior Lighting Designer [cid:image001.png@01D69B12.731F0E20] 240 E. Morris Ave, Suite 200 Salt Lake City, Utah 84115 O. 801.534.1130 D. 801.924.5541 M. 702.523.2187 DTibbitts@envisioneng.com www.envisioneng.com ¦ ¦ Trask will you please respond the the question the Electrical Engineer. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Trask Johnson | Wilkinson Electric Inc | 10/05/2020 |  |  |  |  | Closed | 10/12/2020 | 10/06/2020 | 10/05/2020 | 10/05/2020 | 10/05/2020
724 |  | 0 |  |  | Request for Information | Drain at Dock Lever | The dock leveler submittal 111319.01.01 shows a drain at the center of the dock leveler pit. (see attached from the submittal). Please advise if a drain line is to be installed at the dock leveler as shown in the submittal and provide requirements for the drain and the pipe routing. |  |  |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Mechanical Engineers |  | 10/05/2020 |  |  |  |  | Closed | 10/12/2020 | 10/06/2020 |  | 10/05/2020 | 10/05/2020
725 |  | 0 |  |  | Request for Information | CCD 094 Furring Wall Attachment Clarification | CCD 094 calls for furring at the existing perimeter historic stone walls. These walls flake quite easily and some of these furring walls span up to 19' high (level 2 perimeter walls). Please advise more direction of what type of attachment is needed to properly clip 1-5/8" metal stud furring to the historic stone (wall type A) or through the historic plaster to historic stone (wall type B). Also, please advise what type of bridging is necessary for the furring (e.g. black iron every 4' o.c.). |  | Our recommendation is to you use 1-5/8" 20ga studs with black iron every 4' starting at row 2. We propose installing clips to studs/black iron @ 4' o.c. where the black iron occurs midspan (i.e. row 10) and attaching the clips to the sandstone or through existing plaster with 3/4" x 6" screw anchors. ¦ Aaron, Please provide the options we talked about on the phone. |  |  | High | Aaron Bowers | Pete King Commercial | Aaron Bowers | Pete King Commercial | 10/05/2020 |  |  |  |  | Closed | 10/11/2020 | 10/13/2020 | 10/09/2020 | 10/06/2020 | 10/05/2020
726 |  | 0 |  |  | Request for Information | Hose Bibs at Sump Pit Locations | TFM is requesting that hose bibs be provided at all sump pit locations. Please advise if these are to be provided and provide design requirements. |  | Hose-bibs will be added as requested as part of CCD-029R.5. ¦ ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 10/06/2020 |  |  |  |  | Closed | 10/13/2020 | 11/18/2020 | 11/14/2020 | 11/17/2020 | 10/06/2020
727 |  | 0 |  |  | Request for Information | Stair Treads | Please clarify notes on stair tread details in CCD 077. Detail notes ask for sample of stair tread with carborundum. Please clarify if the carborundum are the groves that are being cut into the stair trend nosing. Another option would be to fill the grooving with a carborundum material. |  | The intent is to see a mockup of the stair tread with the empty grooves, and also a mockup with the grooves filled with carborundum. ¦ Typically what we have seen prepared for the abrasive strips is a mix of 1 part UV rated epoxy to 4 parts silicon carbide. Please provide a mockup for review and approval. ¦ After searching through options for carborundum stair nosing it is clear that there are thousands of different products on the market. The information provided is unclear as to what the architect would like to see for a sample. Please specify a product and model so that a sample can be prepared with what is desired. Thanks, Bob |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 10/06/2020 |  |  |  |  | Closed | 10/13/2020 | 11/20/2020 | 11/13/2020 |  | 10/06/2020
728 |  | 0 | 221319 |  | Request for Information | Baptistery Floor Drains | TFM is requesting that the baptistery floor drain sumps be stainless in lieu of the specified cast iron. Please advise if stainless floor drain sumps are to be provided and provide specifications. |  | VBFA recommends that the owner decide whether to upgrade the type FD-1 floor drains inside the font room, shower areas and locker spaces of level 0.5. The upgrade would be from a cast iron body with nickel-bronze strainer to an all stainless steel product. Stainless steel is a more durable material but is also more expensive. There are currently (32) FD-1 type drains specified for the affected areas. Please see below for some approximate costs per drain. • Cast iron body with nickel-bronze hinged grate (basis-of-design) - $400 each. • All stainless body with hinged grate - $870 each ¦ The floor drains are to be installed as specified. In addition, the contractor is to verify that the procured floor drains satisfy all requirements from the project specifications. ¦ Please advise if we should proceed with the stainless floor drains. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Eric Jamison | CORPORATION OF THE PRESIDING BISHOP OF THE CHURCH OF JESUS C | 10/06/2020 |  |  |  |  | Closed | 10/13/2020 | 11/25/2020 | 11/23/2020 | 11/17/2020 | 10/06/2020
729 |  | 0 |  |  | Request for Information | Clarification of Exit Sign type and locations | In some locations exit signs are labeled 'X1' (single faced) where it appears they should be 'X2' (double faced). Also, some exit signs may be drawn in the wrong location. | Examples of 'X1' exit signs that should be 'X2' include but are not limited to: EL101E Rm 184. Exit sign with 2 arrows facing West. EL100C between Rm 075 and Rm 077 is not clear which direction is the exit. EL100A the exit sign in doorway (052) from Lobby 052 into West Staircase is labeled 'X2', while similarly located exit signs (EL102A Rm 201, EL103A Rm 301, EL104A Rm 401, and EL105A Rm 501) are labeled 'X1'. On page EL100B the South West doorway (015A) between Worker Training Room 015-1 and the corridor to vestibule 005 has exit signs on both sides of the doorway, but none over the doorway (005) between said corridor and stair lobby 024-B. | EL101E Rm 184, exit sign should be double face. EL100C Rm 075/077, in reference to the code plan, the exit is through the shower door to the right. EL100A 052, in reference to the code plan, the exit shall be X1 as shown similarly on the upper floors. EL100B vestibule 005, exit sign shall be placed over doorway to Stair 1 Lobby 024B. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 10/06/2020 |  |  |  |  | Closed | 10/25/2020 | 11/09/2020 | 10/26/2020 | 10/07/2020 | 10/06/2020
730 |  | 0 |  |  | Request for Information | Electrical run to SDMH #10 | Before the project started SDCO #11 had a pump that would pump ground water from SDCO #11 into the storm drain system. There is no electrical in the plans to run power to this SDCO in the plans. If this is the intent to have power ran to this man hole there may be accociated costs. |  | Electrical was unaware of the existing pump. Please provide electrical specs on existing pump, location of pump and detail of existing electrical circuit feeding pump so new electrical service can be determined. ¦ We are fine with routing power from the landscapers shed. Since the landscapers shed does not have a power panel, provide additional circuit from L1P0A for the pump. ¦ ¦ I attached a picture of the old pump spects. The old pump worked when it was removed but it is corroded and I am not confident that it will continue to work after sitting from being removed. I would recommend a new pump be installed. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Electrical Engineers |  | 10/06/2020 |  |  |  |  | Closed | 10/13/2020 | 11/09/2020 | 10/29/2020 | 10/07/2020 | 10/06/2020
731 |  | 0 |  |  | Request for Information | LV switches and T-stat Typical Detail | There is no typical detail with measurements for LV switches and T-stats in 4th floor rooms 409, 411 (East Vestibules), and 410 (GA Lounge). | It is proposed that these devices be installed 6" on center from existing, historic door casework. This would allow room for cutting and chipping into the plaster and stone wall without being too close to the wood casework risking damage, while at the same time being a comfortable distance from the casework for seeing and operating the switches from the doorway. Heights of these devices would remain consistent with the general specifications of 48" on center AFF for switches, and 60" AFF for non-adjustable T-stats. See attached detail. | 8" from outer edge of casing to light switch and t-stats is correct. See attached General Notes on AE4000 sheets. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 10/06/2020 |  |  |  |  | Closed | 10/09/2020 | 10/22/2020 | 10/20/2020 | 10/07/2020 | 10/06/2020
732 |  | 0 |  |  | Request for Information | St. George Temple Signage | What is meant by the word “dimensional” in the phrase “Cast dimensional characters” in specification reference 101419-1-1.2-1(I don’t want to assume that it means one thing, when an architect or designer meant something else.) Knowing the answer to this question will also likely answer the desired thickness question too. A section through the character(s) would be helpful. Material: Specs indicate “Cast Bronze" Samples: specifications indicate that there needs to be a full-size sample of each type of dimensional character. There are 23 different characters required, some of those are required in 2 different sizes. There are a few ways to read and understand this requirement. Please advise. I have attached a break down of the sizes/quantities of each letter/numeral/symbol that are needed on this scope. In summary there are 87 castings required to be made from 32 patterns. |  | Please refer to ASI 047 for response. |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 10/06/2020 |  |  |  |  | Closed | 10/13/2020 | 12/02/2020 | 11/23/2020 |  | 10/06/2020
734 |  | 0 |  |  | Request for Information | Mounting to stone wall | is there a typical detail for mounting items such as electrical panels to the stone wall? if not could we get one or product we need to be using? Please Advise. |  | There are no particular details for mounting items to these walls. However, we do recommend Hilti Re 500 V3 epoxy anchors be used for these applications. All anchors should have 8" min. embedment when attached to the sand stone walls. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 10/07/2020 |  |  |  |  | Closed | 10/14/2020 | 10/14/2020 | 10/13/2020 | 10/07/2020 | 10/07/2020
735 |  | 0 |  |  | Request for Information | Email Art Work and Mirror Backing | We are prepping for plaster and finishing up any demo for Art work and mirrors. At this time on the 5th floor and 3rd floor. We are in need of backing placement for all rooms and hall way. The attic Access has been chanced from the original plan. They re now centered between the bulkheads in the hall way. Please call me if you need. I am happy to help with anything you need |  | This has already been taken care of by Dave and can be closed out. |  |  | High | David Adams | Westland Construction, Inc. | Interior Designer |  | 10/07/2020 |  |  |  |  | Closed | 10/11/2020 | 11/05/2020 | 11/04/2020 |  | 10/07/2020
736 |  | 0 |  |  | Request for Information | Water Softener Valves | The new Culligan water softeners were supplied with galvanized piping to a cast iron head valve. The TFM group is requesting the piping be replaced to Niron and the valve be replaced with a bronze type. Attached is the requested bronze valve information provided by the TFM group along with the pricing to supply the (2) valves and adapters. There will also be a cost from the subcontractor to install these valves and adapters as well as to provide and install the Niron piping. Please advise how you would like us to proceed. for reference we have attached the product data for the water softener. |  | VBFA is in agreement with the TFM that the water softener valve and piping should be replaced given the history with the previous unit. However, please verify with the owner if it is acceptable to spend the money to upgrade the valve and piping for the water softener. |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 10/08/2020 |  |  |  |  | Closed | 10/15/2020 | 10/26/2020 | 10/23/2020 |  | 10/08/2020
737 |  | 0 |  |  | Request for Information | Wall Dimension Conflict | Please advise if we are to use the dimension off of Sheet AE4013 (10'-2 1/2") or Sheet AE140. This wall has already been framed in using the Dimension from sheet AE140 (11'-4"). |  | Please see the attached added revised sheet AE140 that was missing from CCD-96 showing the lengthening of the wall. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/08/2020 |  |  |  |  | Closed | 10/11/2020 | 10/12/2020 | 10/09/2020 |  | 10/08/2020
738 |  | 0 |  |  | Request for Information | VC remaining sidewalk on east side | On the civil page C.5 the side walk on the east side of the VC is not marked for demo. On landscaping page LP 101 the landscaping conflicts with the sidewalk. There is also a door that meets up with the side walk but the sidewalk extends north past the door. How much of the sidewalk if any needs to stay? |  | Civil Sheet C.5 shows the correct location for the demo and retention of portions of the sidewalk on the east side of the Visitor's Center building. Please follow their plan. Updates to the planting plan and landscape site layout plan match with Civil's drawings. The updated site and planting plan are in CCD088 which will be issued soon. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 10/09/2020 |  |  |  |  | Closed | 10/16/2020 | 10/20/2020 | 10/13/2020 | 10/13/2020 | 10/09/2020
739 |  | 0 |  |  | Request for Information | East Historic Tower Wood Structure Condition | At the base of the fiber glass dome at the east Historic Tower the existing wood framing is rotted at a few different locations. See attached photos. Please advise how to proceed. |  | This was discussed while Matt McBride was on site and it was determined that all of the joists and the edge framing need to be removed to eliminate the rotting wood. Westland agreed to remove the flashing just below the dome to determine if the wood can be removed from the outside of the tower and allow access to replace the joists. ¦ this is time sensitive |  |  | High | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 10/12/2020 |  |  |  |  | Closed | 10/15/2020 | 10/20/2020 | 10/19/2020 | 10/12/2020 | 10/12/2020
740 |  | 0 | 230000 | M100B | Request for Information | Exhaust Air at Laundry 056 | Drawing M100B, laundry room 056. The exhaust air as currently shown to be installed will not fit into the vertical above ceiling space as designed. See attached shop drawings showing this. | Per the attached drawings, we suggest a new routing of the exhaust air duct over the adjacent room as shown, with an additional request to lower the ceiling by 6" to allow the exhaust duct to clear the wood beam above. Please advise. | This item will be resolved as part of CCD-098. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/09/2020 |  |  |  |  | Closed | 10/19/2020 | 11/16/2020 | 10/29/2020 | 10/13/2020 | 10/12/2020
741 |  | 0 | 230000 | M100 | Request for Information | Transfer Air Duct Boots-Annex | We are in receipt of and have reviewed RFI# 666 and CCD#028R3 scope clarifications and direction. It appears that per these two directives it is acceptable to eliminate all of the transfer air boots at Annex Bldg, level 0 and 1. Please confirm. | If it is not the intent to eliminate the transfer air boots in their entirety at the Annex Bldg, please provide information clarifying which boots are to be eliminated and which are to remain. See attached clouded drawings for clarification along with keynotes 14 and 15 indicating coordination to occur with design team to locate these transfer air locations. | See comment from Brian Oswald, VBFA dated 13-Oct-2020 ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 10/13/2020 |  |  |  |  | Closed | 10/20/2020 | 10/14/2020 | 10/13/2020 | 10/13/2020 | 10/13/2020
742 |  | 0 | 230000 | M603 | Request for Information | Dryer Fan Information | Per RFI# 273 response a dryer fan tagged EF-DB-1 is called to be provided at laundry 028. This equipment is called for on current drawing M100. The equipment schedule drawing M603 does not appear to have this fan shown. Please provide a fan schedule, model, etc for equipment tagged EF-DB-1. |  | The dryer booster fan EF-DB-1 information has been updated and will be issued with CCD-028 R.4. ¦ Please disregard my last comment. I meant to reference to CCD-028R.4 not 024R.4. |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 11/13/2020 |  |  |  |  | Closed | 11/12/2020 | 11/19/2020 | 11/13/2020 | 11/10/2020 | 10/13/2020
743 |  | 0 |  |  | Request for Information | Aphid infestation in the pecan trees | Description: Aphides have returned to the existing pecan trees on site. The aphid deposits are having an adverse effect and are glazing the new sidewalk, rock mulch, and trees/shrubs. This will be a consistent clean up and upkeep effort for the temple. In an effort to reduce the work load on the temple and protect the new plantings and hardscape and maximise the patron experience I have suggested three possible solutions below. 1. Do nothing and plan for the temple to continued clean up and maintenance from the aphid effects. 2. Chemically treat the pecan trees to kill the aphides. 3. Remove the pecan trees. |  | Due to the historic nature of the trees, removal will not be an option. CRSA and MGB+A will find an systemic chemical treatment that will address the aphid problem and allow the fruit to remain safe for consumption. As soon as the appropriate application is identified treatment can begin. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 10/13/2020 |  |  |  |  | Closed | 10/20/2020 | 10/20/2020 | 10/14/2020 | 10/13/2020 | 10/13/2020
744 |  | 0 |  |  | Request for Information | Dome Exterior Light Fixture Supporting | The existing support for the dome exterior lighting creates some problems: 1- The feet used had 5 penetrations each (16 total feet) that created multiple potential leak points (see attachment "Dome, old feet for light fixture support") 2- The feet and deep Unistrut used were built to support much larger and heavier fixtures than the LED ones we are now using. They were bulkier and larger than now needed, and were therefore more intrusive and visible from the ground. | It is proposed that the dome be patched and fixed where the old feet were mounted, removing 80 holes. Then we would install a smaller, more streamlined fixture support that would work well with the new LED light fixtures. They would be much less visible from the ground, and each would only entail (2) 3/8" diameter holes for mounting through the dome. The new holes would be sealed inside and out with polyurethane sealant. (see attachments "Dome light detail 1.0" and "Dome Exterior Light Mounting Detail 2.0" | The recommended mounting sounds like it has been well thought out; however, the new mounting method must be able to secure the LED Light Fixtures to the Dome in whatever historically expected winds (sustained and gusts) may occur in the immediate area. Has the Project Structural Engineer been consulted on the new mounting method? ¦ We recommend increasing the diameter of the new fender washer above and below the dome to match the diameter of the old feet used in the previous attachment. ¦ ¦ Will you provide your input on what we are asking in this RFI |  |  | High | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 10/15/2020 |  |  |  |  | Closed | 10/18/2020 | 10/29/2020 | 10/27/2020 | 10/20/2020 | 10/15/2020
745 |  | 0 |  |  | Request for Information | Window Sill Flashing RFI | Are the windows sill flashings shown in the attachment necessary? |  | Please refer to the revised window flashing details recently sent in CCD 113. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/15/2020 |  |  |  |  | Closed | 10/18/2020 | 12/02/2020 | 11/30/2020 |  | 10/15/2020
746 |  | 0 |  |  | Request for Information | Site dock screen wall details | Reference sheet AS401, AS501, AE148, C.6, S004 1) Sheet AS401 references screen wall details A1,A2/AS501 which shows a footing/stem wall and CMU above. Civil plans C.6 note 8 show straight curb (6"x18") per detail C.13 detail F. Which is the correct detail? 2) If the CMU screen wall is required we assume it would be a type MW-1 per note 1 on S004. Please clarify footing size and reinforcing requirements if needed beyond what is shown on C.13 detail F 3) Please provide elevations and dimensions for gates/dumpster and wall/column popouts if required as shown on AE148. Per detail A2/AS501 the CMU appears to be on a stem wall that pop outs at the column locations. Dimensions needed for these columns. 4) Please provide bollard base details if required or do they post install to the slab with anchors? Reference note 32.08 on AS401. |  | See attached for screen wall and footing requirements. For all other questions, refer to Architectural. ¦ Refer to ASI #54 for additional information in response to this RFI. ¦ Please provide final direction on what we need to plan for. Will this be issued as a CCD? Please clarify screen wall dimensions, elevations, buttress details at stem wall and CMU architectural details. ¦ Looks like ARW got their portion now it's with CRSA. |  |  | Medium | Judd Bundy | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 10/19/2020 |  |  |  |  | Closed | 10/26/2020 | 11/05/2020 | 11/04/2020 | 10/28/2020 | 10/19/2020
747 |  | 0 |  |  | Request for Information | Outlets Laundry Rm. 028 | Sewing machine cabinets are in a different location on the electrical plans than the architectural plans (see attachments) outlets behind commercial washing machines don't have circuit call out. do these outlets need to be a specific elevation (see attachments) outlets on west wall are located at shelving, should they be moved to the sides? (see attachments) |  | Move outlets for sewing machines to match up with architectural locations. mount outlets behind washers at +48" for soap dispensers. Coordinate exact locations with architect prior to rough in. Circuit is L1P0A-14 Yes move outlets to the side of shelves. ¦ See response from Envision. Outlet locations for the soap dispensers TBD. ¦ Plans to be updated as part of CCD-054.4R1. ¦ ¦ 1. Please confirm the Arch. layout that is to be used. The ones on Sheet AE4007, and Cabinetry Submittal 064023.07.01 or Sheet EP100 and AE100. (see attached RFI 747_Outlets Laundry Rm. 028) 2. Electrician can follow the direction given. (see attached RFI 747_Outlets Laundry Rm. 028) 3. When reviewing the cabinet drawings, we noticed that the wall in question has had a cabinet box added. This is removing the wall space needed for the install of the Outlets on the side of the cabinets. (see attached RFI 747_Outlets Laundry Rm. 028) |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 10/27/2020 |  |  |  |  | Closed | 10/22/2020 | 11/10/2020 | 10/29/2020 | 10/19/2020 | 10/19/2020
748 |  | 0 |  |  | Request for Information | Historic mat slab pour sequence | Please advise if the attached sequencing and locations of the construction joints in the historic basement will be acceptable. |  | The proposed sequencing is acceptable. Please see attached sketchs for comments and construction joint detail requirements. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 10/19/2020 |  |  |  |  | Closed | 10/22/2020 | 10/20/2020 | 10/19/2020 | 10/19/2020 | 10/19/2020
749 |  | 0 |  | AE4203 | Request for Information | Mirror Backing | Please confirm that we are to have TID remove the plaster behind the mirrors in the historic bathrooms. This will allow us to install the backing required to support the mirrors. For reference we have included sheet AE4203. A prompt response on this will be appreciated. |  | The sheet referenced is AE4503 not AE4203. The restrooms are to have new framed walls behind the Lavs and mirrors on the 3rd and 5th floors That blocking can be added. The existing plaster is to remain behind the new wall framing (where occurs) and was not intending to be removed. See the attached plan images. ¦ See previous comment regarding the restrooms. In the Instruction rooms, the plaster is to be minimally removed at locations from stud to stud where mirrors/ artwork are located to provide access to install new blocking. ¦ please revise response |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/20/2020 |  |  |  |  | Closed | 10/23/2020 | 10/21/2020 | 10/20/2020 |  | 10/20/2020
750 |  | 0 |  |  | Request for Information | E. tower Ext. Lighting Support 1st level down from dome | The current direction is to remove and re-install the existing light fixtures on the existing supports. The first level down from the dome has lighting supports that are corroded, create dubious roof penetrations (see attachment "Exterior lighting support 1st level below dome"). Could these supports be removed and replaced? | It is proposed that the existing light fixture supports be removed on this level and replaced with supports similar to those on the 2nd level down from the dome (see attachment "Exterior lighting support 2nd level below dome"). This support method eliminates penetrations through the roof, is much less prone to leaking, and makes it much easier to re-roof, and maintain roofing. | The recommended mounting sounds and appears to have been well thought out, and we do not have any problems with the recommendations, but as with the previous tower light mounting recommendation the new mounting method must be able to secure the LED Light Fixtures to the Dome in whatever historically expected winds (sustained and gusts) may occur in the immediate area. We would again recommend that the Project Structural Engineer been consulted on the new mounting method. ¦ We take no issue with what is being proposed. We recommend attaching the angle to the post using a minimum of (2) 1/4"x4" long lag screws. ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 04/01/2021 |  |  |  |  | Closed | 10/27/2020 | 04/01/2021 | 11/12/2020 | 11/11/2020 | 10/20/2020
751 |  | 0 |  |  | Request for Information | Relief Air Plenum at Mech RM 001_020A_and 032 | The mechanical contractor brought up the concern that Mechanical Rooms 001, 020A, and 032 are designed to serve as a relief air plenum and wanted to ensure they were air tight to meet the design intent. Please advise if any modification is needed at these spaces to meet the air tight assembly design intent. At north Mechanical Room 001, door opening 002 is called out as an concrete opening with no door. Since MEP piping and conduit are routing through that door way, please advise how to proceed to provide the air tight space at this location. | Provide a framed wall assembly at storage 003 starting east of door 003A and running north to just east of door opening 002. | Please refer to the attached pdf "20201120_SGT_RFI-751_Mechanical". Doors are to be provided where indicated between North Mechanical [001], Electrical [002] and Storage [003]. The doors will officially be added in a forthcoming CCD. In addition, the drywall around the mechanical rooms shall extend to the bottom of deck as indicated in the attached pdf "20201120_SGT_RFI-751_Mechanical". ¦ Please refer to CCD 101 showing new doors that were added. ¦ ¦ ¦ |  |  | High | Mechanical Engineers |  | Russ Farley | Architectural Building Sup | 12/01/2020 |  |  |  |  | Closed | 11/12/2020 |  | 12/16/2020 | 01/21/2021 | 10/21/2020
752 |  | 0 |  |  | Request for Information | Confirm Lighting Dimensions Rms under East Tower Flrs 2-4 | As per walkthrough and conversation with Kyle Welch and Scott Gilberg with CRSA we modified the Lighting dimensions in rooms 219, 318, and 410 which are all located under the East tower. Adjustments were made to center the lights on windows, doors and chandeliers, miss steel 'I' beams, and to make dimensions consistent and equidistant. These dimensions were made to conform with the expressed intent of the Architect concerning the lighting layout. Can we confirm that our adjusted lighting dimensions are acceptable? | See attached drawings for our adjusted lighting dimensioned layouts. | Looks correct. Some lighting in the GA Lounge were not dimensioned from the walls at the corner locations. When installing verify that the dimensions are equal off both walls. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 10/21/2020 |  |  |  |  | Closed | 10/28/2020 | 10/28/2020 | 10/23/2020 | 10/23/2020 | 10/21/2020
753 |  | 0 |  |  | Request for Information | Elevator 5 shaft layout error | See mark up sheets AE141A and AE142. As discussed onsite with Kyle (CRSA) and Zach (ARW) we have an layout error with the north side of elevator shaft 5. The attached sheets provide the actual dimensions. 1) As reviewed please verify if the shaft can remain as is or if it needs to be re poured? 2) ARW if the wall needs to be adjusted please review the attached sketch and advise if this proposed fix is acceptable? |  | The proposed sketch is acceptable. Please provide #3 hooked dowels into the cut face of the wall in a manner similar to detail 18/S221 that was used at the loading dock area. |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 10/23/2020 |  |  |  |  | Closed | 10/29/2020 | 11/02/2020 | 10/29/2020 | 10/29/2020 | 10/23/2020
754 |  | 0 |  |  | Request for Information | Jacket wall dimensions grid H5 stair | As reviewed onsite please reference RFI 605 and mark up from sheet S101B. 1)Please provide end of wall dimension for the 8" jacket wall that supports the slab on metal deck. Top of wall is at elevation 99'-5 1/2" per RFI 605 response. |  | See attached mark-up for the end of wall location. ¦ |  |  | High | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 10/23/2020 |  |  |  |  | Closed | 10/29/2020 | 10/27/2020 | 10/27/2020 | 10/23/2020 | 10/23/2020
755 |  | 0 |  | 1/P702 | Request for Information | Gas Meter | US Mechanical reached out to Dominion Energy to coordinate resizing the gas meter (see note in detail 1/P720). Based our the current Gas Schematic 1/P702, Dominion is requiring an 18 to 20 foot meter set. 1) Please advise where the new meter is to be located. 2) Will the line sizes in the building need to be redesigned due to any added length between the main regulator and any sub regulators? Please advise and provide any modifications to the gas schematic 1/P702. 3) There is currently no call out for an earthquake valve on the main service before it enters the building. Will this be required? Please advise and provide plans and specifications. |  | It has been proposed to move the gas meter to the south side of the Annex along grid A2 and between grids AG and AH. The meter location is currently being updated with landscaping and will be issued formally as part of CCD-029R.6. ¦ We will issue this to the Subcontractor when we receive CCD-029 R.6 |  |  | High | Jason Fullmer | Westland Construction, Inc. | Mechanical Engineers |  | 10/23/2020 |  |  |  |  | Closed | 10/29/2020 |  | 12/17/2020 | 10/23/2020 | 10/23/2020
756 |  | 0 |  | EP100 | Request for Information | Annex Basement outlet locations | Sheet EP 100 shows plugmold and above counter outlet at room 042 are both needed? location/elevation? length of plugmold? Sheet EP 100 Breekroom 010 has a counter/w sink it shows no backsplash we need elevation of outlets above this counter. it also shows microwaves at both 60" and 24" is this correct? Sheet EP 100 Grab and go 011 at POS 1 outlet above counter 1 outlet and data below, at south end of same counter 1 outlet and data bellow counter 1 outlet above is this correct? Sheet EP 100 Lav sinks show a Jbox for sensor power (P13) we need a typ location for these. (see attachment for all of these questions) |  | See attached shop elevation image for location of outlets/plugmold on east wall of shop. Refer to detail 1/EP501 for mounting heights of all devices including those above counters. Microwave locations have been adjusted, please move all (3) microwave outlets to be at +60". Yes outlets are provided below counter for additional equipment connections. Faucet sensor heights should be coordinated with plumbing installer. We typically see the outlets mounted at +20". In a location not readily visible to patrons. ¦ 2- Breakroom countertops will have a 4" backsplash. Outlet heights will need to be installed as specified on EP501. 3- We will need to add an additional Data outlet above the POS counter next to the outlet. See response and attachment from Jessica with Envision as well. ¦ Please clarify power data locations from note 3 (above counter, in cabinet and below counter). |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 10/23/2020 |  |  |  |  | Closed | 10/29/2020 | 11/09/2020 | 11/03/2020 | 10/29/2020 | 10/23/2020
757 |  | 0 | 126700 |  | Request for Information | Arm Rest Attic Stock | Please advise the required attic stock for the opera seating. | The TFM has requested that we have enough attic stock to replace all the arm rests in a room plus 10 additional. They have also requested that the arm rest material be changed from hardwood to Corian. | Armrests need to be wood. ¦ ¦ Please update per interior design meeting. | Interior Designer |  | Medium | David Adams | Westland Construction, Inc. | Interior Designer |  | 10/23/2020 |  |  |  |  | Responded | 10/30/2020 |  | 02/24/2021 | 11/04/2020 | 10/23/2020
758 |  | 0 |  | AE 124, GA005 | Request for Information | Ceiling Framing RM 410 Study | Sheet AE124 calls for a ceiling type C2 finishing out at 17'-6". From floor to LVL framing we have 17'6" already. Should the C2 ceiling be provided, lowering the ceiling height or should the gyp and plaster be applied directly to the LVL framing? Please advise. This would lower the ceiling to 17'-2" if C2 ceiling is to be installed. | Lowering the ceiling would help accommodate the MEP rough in. | Please use 1/2" resilient channels between the LVL joists and 5/8" Gypsum board ceiling in Room 410. This is to provide an additional STC sound rating. CRSA is aware that the ceiling will be a few inches lower than what is reflected in the current drawings. ¦ Per conversation with Scott and Kyle we are to use the 7/8" hat channel and sound batts between Ceiling Joists. |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/21/2020 |  |  |  |  | Closed | 10/30/2020 | 01/05/2021 | 01/04/2021 | 10/26/2020 | 10/26/2020
759 |  | 0 |  | M411 | Request for Information | Remote Supply Lines for Chemical Treatment Station | TFM is requesting remote supply lines be provided from the mechanical courtyard down to the existing chemical treatment station in the boiler room to allow for the chemicals to pumped down to the station rather than barrels being transported to the station. | A possible solution would be to route (2) 3/4 inch Niron pipe lines, one for bio and one for phosphonate, as shown in the attached. Please advise and provide direction as needed. | Please see the response in the markups of the attached pdf "M411 - MECHANICAL ENLARGED PLANS & SECTIONS_VBFA". ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Mechanical Engineers |  | 10/26/2020 |  |  |  |  | Closed | 11/02/2020 | 12/02/2020 | 12/01/2020 | 10/28/2020 | 10/26/2020
760 |  | 0 |  |  | Request for Information | Font Pit New Design - Las Vegas Rock Material | During the last Stone Committee meeting on October 13-14, it was brought up that a new design would be issued for the Font Pit. Please provide us the new design so we can price the stone on this Font Pit. Thank you, |  | PLease reference CCD #105- the new tile patterns/details are issued here |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 10/27/2020 |  |  |  |  | Closed | 10/31/2020 | 11/10/2020 | 10/29/2020 |  | 10/27/2020
761 |  | 0 |  |  | Request for Information | Ashlar Pattern Dimensions | Please confirm the dimensions of the FS1 - Sierra Smoke Ashlar Pattern from Las Vegas Rock. Assuming a 1/8" joint, the stone sizes would be: 7-7/8" x 7-7/8" 7-7/8" x 15-7/8" 15-7/8" x 15-7/8" 15-7/8" x 23-7/8" Please confirm if this is correct. Thank you, |  | These sizes are in the acceptable range. Contractor to install with 1/8" grout joints. |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | CRSA ARCHITECTURE |  | 10/27/2020 |  |  |  |  | Closed | 10/31/2020 | 12/08/2020 | 12/08/2020 |  | 10/27/2020
762 |  | 0 |  |  | Request for Information | Ceilings Replaced in Rooms 409, 410 and 411 | Please confirm that due to the ceiling in rooms 409, 410 and 411 being demoed along with the crown that we are to replace the historic crown with new GFRC crown matching the historic crown. |  | The crown in rooms 410 and 411 are to be preserved and not removed. Crown in room 410 should of been scanned prior to removal. It will be replaced with GFRG crown that will match the historic one that was removed. The GFRG medallions for these 3 rooms will be covered in a future CCD. ¦ Correction, The crown in rooms 409 and 411 are to be preserved and not removed. Not room 410 per my previous response. ¦ We will close this when the future CCD is issued. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/11/2020 |  |  |  |  | Closed | 10/30/2020 | 12/03/2020 | 11/12/2020 |  | 10/28/2020
763 |  | 0 |  | AE143, AE102 | Request for Information | Lobby 218 Support High Walls | On Levels 2 and 3. please provide direction regarding the support required for the wall running along grid lines H2 and H4. The wall assembly is type 55 as shown on the attached pages. As presently designed we are to install this wall above the existing historical wood flooring that is being cantilevered over the next adjacent joist some 6" to 8" away. |  | See attached sketch for requirements. These clarifications will be issued in a forthcoming CCD 87-R.4. ¦ See CCD87-R.4, Sheet S103 and detail 2/S246 ¦ ¦ I cant find the sketch you said you attached and I cant find it in CCD 087.R4. When you have a second will you give me a call so we can discuss. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 10/28/2020 |  |  |  |  | Closed | 11/03/2020 | 11/13/2020 | 11/12/2020 | 10/28/2020 | 10/28/2020
764 |  | 0 |  | AE503 | Request for Information | Tilt Wall to Concrete Base Connection | Please provide direction as to how the connection between the tilt up wall and the concrete wall are to be done, and the material to be used. |  | Please refer to CCD 34- Buttress Plinth clarifications @ Annex for revised details. ¦ Refer to CCD- 34 revised details showing the portion of concrete to be removed and replaced with new shaped High impact foam EIFS. This also covers filling in the large gaps under the precast panels and concrete walls. ¦ We will close this RFI when we get CCD 034. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/28/2020 |  |  |  |  | Closed | 11/03/2020 | 12/17/2020 | 12/14/2020 |  | 10/28/2020
765 |  | 0 |  |  | Request for Information | Historic Anchor Bolt Layout | Due to scheduling conflicts and In the interest of keeping the schedule would it be acceptable to post install the embeds in the clouded area above? |  | This is a possible option, but please keep in mind the embed plate sizes will likely be larger and there may be more epoxy bolts required than headed studs. This will need to be redesigned if it is desired to use a post installed option. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 10/28/2020 |  |  |  |  | Closed | 10/30/2020 | 10/28/2020 | 10/28/2020 |  | 10/28/2020
766 |  | 0 |  |  | Request for Information | Dock gate details | Related Scope: Site fence and gate Related Documents: AS401, LL510 Description: On AS401 has a gate 32.05. There are no details on this gate like the other gates listed on LL510. Please provide detail with measurements and dimensions for gate 32.05 on AS401. Also, there is no detail for the rolling system and how it should attach to the wall. Does the size and weight of gate 32.05 need a mechanical opening system? And if so power and controls need to be considered. |  | See upcoming CCD 116 for plans and details regarding the sliding gate. ¦ We will close this when we receive the CCD ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 12/17/2020 |  |  |  |  | Closed | 11/15/2020 | 04/01/2021 | 12/17/2020 | 12/17/2020 | 10/28/2020
767 |  | 0 |  |  | Request for Information | Site rebar details modified in submittal | Reference attached submittal 03 2000.08.00 site concrete reinforcing. To avoid questions and issues during special inspections, engineer please verify that the following details are correct as noted in the site rebar submittal: 1) 6" walls at north fountain per detail 2/LL507 are single curtain of rebar as noted in the submittal sheet S-1 2) The site wall footings on detail 3/LL510 were changed in the submittal sheet S-1 and are now 4'-0" wide with #5 @ 12" T&B and 8 #5 cont (4 T&B) 3) Monument wall section on 4/LL510 will be a single curtain of rebar not a double as shown on submittal sheet S-2 |  | Confirmed ¦ |  |  | Medium | Judd Bundy | Innovative Concrete LLC | Structural Engineers |  | 10/28/2020 |  |  |  |  | Closed | 11/04/2020 | 10/29/2020 | 10/29/2020 | 10/29/2020 | 10/28/2020
768 |  | 0 |  |  | Request for Information | Control Joints | From past experience on other temples, we have not installed control joints in walls that run greater than 30'. Please confirm we are not installing control joints in walls spanning longer than 30' for this temple. In the specification is referenced ASTM C840 for reference I have attached the ASTM to this RFI. |  | No control joints. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 10/28/2020 |  |  |  |  | Closed | 11/04/2020 | 11/05/2020 | 11/04/2020 | 10/29/2020 | 10/28/2020
769 |  | 0 |  |  | Request for Information | Traning room AV | Drawing XE110 show a MA and TS box located in cabinet we need a location, and type of box see attachment |  | TS is a touch panel, which sits in the cabinet. No back box is required for it. t that sits between the two monitors. MA is the junction box for the mixer/amplifier. It is a 3” deep, 4” square box with a double gang plaster ring, and it is mounted flat at the floor underneath the cabinet. Below is direction from the Church AV department. The Touch Screen is free standing and is intended to sit on top of the 30” cabinet. The computer and audio amplifier will be in the cabinet underneath. The junction box in the cabinet should be in the wall at around outlet height and though it may have been originally specified as a 4-square box, it might be best to enlarge it to a 12” x 12” box to accommodate the conduits and cable that should be coming into it. There should be a conduit from this cabinet backbox to each monitor backbox and should perhaps be up-sized to a 1-1/4” conduit. There should be a power outlet in each monitor backbox and in the cabinet. The data ports for the training system should be located in the backbox located in the cabinet. Some of this may constitute a change that will need to be run through proper channels, but it will make installation of the training system much easier. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 10/28/2020 |  |  |  |  | Closed | 11/04/2020 | 11/09/2020 | 11/04/2020 | 10/29/2020 | 10/28/2020
770 |  | 0 |  | XE110, EP100 | Request for Information | Annex Basement Electrical | XE110 can we relocate session clock from furred CMU wall to location where laundry workers will be able to see it better (see Attachment) EP100 Can we relocate outlet and wall phone from furred CMU wall that will not accommodate the depth of the box to another location in the room (see attachment) EP100 Panel L1K0A has a S.S. 4X enclosure which is surface mount (for the kitchen) this would protrude into the hallway. we would suggest using a nema 1 enclosure with a flush cover or relocating panel to storage room 003-1 (see attachment) |  | We see no issue with the proposed location. We see no issue with moving devices to the proposed location. We have no issue with relocating the panel into the storage room. Since the panel is already on site with the stainless steel finish we see no reason to change the finish. It is not required but we see no reason to order a new enclosure. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 10/29/2020 |  |  |  |  | Closed | 11/05/2020 | 11/09/2020 | 11/02/2020 | 10/30/2020 | 10/29/2020
771 |  | 0 |  |  | Request for Information | Fiberglass Tower Exterior Paint Clarifications | I need to know which paint we are using on the lower portion of the Fiberglass Tower. Wednesday 10/28/2020 we received ASI 051 which clarifies all primers, tie coats and paints and delineates the areas each are to be applied (See attached ASI 051). Today (Thursday) 10/29/2020 we received a revise and resubmit stating that one of the materials Benjamin Moore Moorgard W103 does not meet spec. However in the ASI, it was laid out as the material to use. We have already purchased materials for this, and started applying it to the building. We need information on how to proceed. URGENT. Thank you |  | Please refer to ASI 51 Exterior Paint Clarification. ¦ Submittal stamped 11/2/2020 had approved the Moorguard. ¦ Please revisit the Question. The ASI is saying to use Moorguard, but Moorguard was rejected in the submittal. they are wanting some Clarification on if they are to use the Moorguard or if something else needs to be provided. As a side not they have already purchased the Moorguard for this area. |  |  | Medium | Ader Sanchez | Unlimited Designs Inc. | CRSA ARCHITECTURE |  | 10/29/2020 |  |  |  |  | Closed | 11/05/2020 | 12/08/2020 | 12/04/2020 |  | 10/29/2020
772 |  | 0 |  |  | Request for Information | Wood Base Level .05 | West tower rooms 051, 052, 053, 051, S-3, level .05, finish schedule call for wood base type B1, (stone with wood cap) detail C1/AE570. Our shop drawings are approved showing base B1 in these rooms. CCD 40 changed the finish floor in these rooms to be LVT flooring. I do not think you still want stone base where there is LVT flooring. Please clarify wood base type in these locations. |  | Please see CCD40 R.1, R.2 and R.3 showing revised finish plans and finish schedule changes. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 10/29/2020 |  |  |  |  | Closed | 11/12/2020 | 12/17/2020 | 12/15/2020 |  | 10/29/2020
773 |  | 0 |  |  | Request for Information | Interior windows Annex and West Tower type A, AA, D, G | CCD 085 deleted the wood trim around the windows, however CCD 85 did not address how the vertical and horizontal structure post are to be covered or trimmed out at window type A, AA, D, G. |  | These windows have integrated structure and will be trimmed bout my Re-view Windows. See attached Window Shop drawing. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 10/29/2020 |  |  |  |  | Closed | 11/12/2020 | 12/17/2020 | 12/15/2020 |  | 10/29/2020
774 |  | 0 |  |  | Request for Information | Radio Antenna on Annex Roof Location | Where should the roof penetration for the radio antenna be located, and where should the antenna be installed? | As per conversation with Kyle Welch it was determined to penetrate the lower roof on the West side of the Annex roof, close to the wall of the raised center section. The conduit penetration through the roof would have a weatherhead installed, and the antenna would mount to the wall with unistrut. The top of the antenna would either be at or below the center roof level, or possibly be slightly higher. This location provides ample coverage for the temple, grounds, and ancillary buildings. It will be virtually unseen from the West side of the temple, even from the West side of 200 E in front of the temple president's house. Cory - TFM would like to have it just above the roof line to insure that it will be able to broadcast on to the east side of the Temple Grounds. | We are Ok with the proposed location. It sounds like thought has been put into this not being visible as much as possible from major Temple entrances. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 10/30/2020 |  |  |  |  | Closed | 11/02/2020 | 11/05/2020 | 11/02/2020 | 10/30/2020 | 10/30/2020
775 |  | 0 |  |  | Request for Information | Exit Sign Confirming RFI | Please confirm attached plans with notes for all of the exit signs. These were reviewed with CRSA on Monday, October, 26th. Locations. X1/X2 = single or double face. Recessed wall or ceiling mount, and surface mount options. Directional arrows: NA = no arrows, LA = left arrow, RA = right arrow, etc. |  | Please refer to CCD-044 R3 confirming exit signs. ¦ Please refer to CCD-044R.3. ¦ We will close this RFI when we get CCD 044R3 |  |  | Medium | David Barney | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 10/30/2020 |  |  |  |  | Closed | 11/12/2020 | 12/11/2020 | 12/08/2020 |  | 10/30/2020
776 |  | 0 |  |  | Request for Information | Baptistry trench drain | Related Scope: Civil/Landscaping Related Documents: LL106, C.8 Description: The trench drain in LL106 at the baptistry plaza does not show any connections to the storm drain system. How does the trench drain connect to the storm drain? Does the trench drain wrap the entire planter wall? Provide direction how the trench drains are to connect to the storm drain system and to what extent/length and locations do the trench drain need to be installed. |  | Sheet C.8 has been updated to show the trench drain connection to the storm drain. See attachment. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 10/30/2020 |  |  |  |  | Closed | 11/12/2020 | 01/21/2021 | 01/08/2021 | 12/15/2020 | 10/30/2020
777 |  | 0 |  |  | Request for Information | Multiple Irrigation questions | Various irrigation questions that corrilate with attached plan page. Orange, does this sod stay in this area? There are currently four valves feeding the irrigation for the park strip sod (in red). These valves are to be used for other irrigation areas, so if the sod remains valves will need to be added. Purple line is the new main irrigation line form RFI 551. Blue line is a proposed lateral line to feed the one valve on the east side of the VC if the valve stays in the same location. Please advise. Red cloud, is a concern that the amount of valves and boxes in this tight area. Green, S&B says that this route will cost less and will have less of an impact on the new plants. |  | Please see our responses in the attached pdf. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 10/30/2020 |  |  |  |  | Closed | 11/12/2020 | 11/19/2020 | 11/13/2020 |  | 10/30/2020
778 |  | 0 |  |  | Request for Information | VC site lighting | Related Scope: Electrical/Landscaping Related Documents: ES200 Description: Per plan page ES200-Site Lighting, in the VC area there is no site lighting located along the sidewalk leading from the east plaza to the VC plaza and there are also no lights in the planter walls. Confirm that there are no wall lights in the VC plaza area? Confirm that there are no light poles intended for the sidewalk between the east plaza and VC plaza? |  | During the design phase we discussed having steplights in the Visitor’s Center Plaza Wall, but many on the Design Team felt that the existing steplights were distracting when looking toward the Temple out of the Northwest windows of the Visitor’s Center. Bollards on the lawn between the East Plaza and the Visitor’s Center Plaza were also thought to be distracting. Additionally, the Sidewalk between the East Plaza and the Visitor’s Center Plaza will be sufficiently lighted with just the light reflected from the Temple, and since this sidewalk is not intended to be used as an emergency egress path no additional lighting is necessary. ¦ See response from David Tibbitts |  |  | High | Zac Givens | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 10/30/2020 |  |  |  |  | Closed | 11/26/2020 | 12/10/2020 | 11/12/2020 |  | 10/30/2020
779 |  | 0 |  |  | Request for Information | Large sidewalk to paver detail | Related Scope: Landscaping Related Documents: LL100 / LL501 Description: Per plan page LL100 the detail designated with purple dashes calls out 2 5/8” lugged paver. But on LL501 detail #3 only shows concrete. Confirm that a paver is intended? If it is the intent to have a paver on the edge of the larger sidewalks designated with the purple dash. Please provide a detail that shows the lugged paver and how it ties into the concrete? |  | See updated details on sheet LL501. The purple dashed line indicate where vehicular rated pavers and/or concrete would need to be located. |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 10/30/2020 |  | 0 |  |  | Closed | 11/15/2020 | 12/10/2020 | 12/03/2020 |  | 10/30/2020
780 |  | 0 |  |  | Request for Information | Training Rm 015 confirming RFI | In training room 015 the box behind the equipment cabinet that receives the conduits for speaker wire, data, and outputs to the monitors is shown as being a 4" square box. The data runs are shown at the monitors, and nothing in the equipment cabinet. There is no dimensioned detail for the outlet location or LV back box behind the equipment cabinet. | In conversations with Brad Justensen and Cole Duke from the church A/V department the following was requested: 1- Replace the 4" square box with a flush mount 12x12x4 J-box. 2- Run both data runs into the 12x12x4 J-box behind the equipment cabinet. 3- In scaling off the plans, including the keyed note 2 on XE110, we settled on the following dimensions (which are shown on the attached drawing): -Install the power outlet at 18" AFF to center, and 11' off of the north wall to center. -Install the 12x12x4 J-box at 18"AFF to center, and 12' 8" off of the north wall to center. Please confirm that this will work with the furniture shown. 4- Due to the amount of cables, including HDMI cables that need to be pulled from the 12x12x4 J-box behind the equipment cabinet up to the boxes behind the 80" monitors, Brad is requesting that those two conduits be upsized from 1" to 1 1/4" EMT. This will likely incur a materials cost as well as an increase in labor. | Design team is in the process of completing a change for the training room. These box and conduit sizes will be included into that change and device locations adjusted for the floorplan changes. |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/03/2020 |  |  |  |  | Closed | 11/08/2020 | 12/10/2020 | 11/12/2020 |  | 11/03/2020
781 |  | 0 |  |  | Request for Information | Custodial Supply Office 007 add outlet | Should there be an outlet added in the custodial supply office 007 on the east wall next to the data outlet shown? Should the data outlet (and power outlet if added) be installed above the counter top, or at 18" AFF to center? If they are to be installed above the counter top backsplash, what is the height? |  | Move standard outlet on north wall to be adjacent to the data outlet. Mount both above counter, at mounting heights shown in detail1/EP501. Coordinate height of counter and backsplash with architect prior to rough-in. ¦ Install outlets 4" O.C. above 4" wide backsplash. ¦ Please advise as to the installation location of the outlet in the Custodial Office. |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/03/2020 |  |  |  |  | Closed | 11/08/2020 | 11/16/2020 | 11/13/2020 | 11/12/2020 | 11/03/2020
782 |  | 0 | 131213 | FP-0801-NORTH-FOUNTAIN.dxf & FP-0161-EAST-FOUNTAIN.dxf | Request for Information | NORTH & EAST FOUNTAIN PRODUCTION DRAWINGS | Please review the included North (FP-0801-WESTLAND) and EAST (FP-0161-WESTLAND) FOUNTAIN production drawings. |  |  |  |  | Medium | Mark Gabriele | Artisan Granite, LLC | Westland PE’s |  | 11/03/2020 |  |  |  |  | Closed | 11/10/2020 |  |  |  | 11/03/2020 | See Other
783 |  | 0 |  |  | Request for Information | Fire protection supply line | Related Scope: Civil / Fire Protection Related Documents: CCD 089 / C.11 Description: The attached document shows a dashed red line showing a proposed route of the fire suppression supply line. The new proposed route for the fire supply line, is to install it as close to the building as possible. It also needs to be supported with brackets and reinforced for the portion that will be suspended when the west stair tower is excavated. Please provide direction on the location of the fire supply line, support bracket design and spacing, and the material for the pipe and 90 elbow that goes into the building. |  | See response from Paul Mogle ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 11/04/2020 |  |  |  |  | Closed | 11/15/2020 | 12/10/2020 | 12/09/2020 | 11/09/2020 | 11/04/2020
784 |  | 0 |  |  | Request for Information | Monument signs elevation | Related Scope: Civil / Landscaping Related Documents: LG201, LG202, & LL510 Description: The monument signs located on LG201 and LG202 have elevations that are unclear. Please clarify the elevation for the top of curb these two signs. On page LL510 there are no dimensions from the top of footing to top of grade. How deep should the footing be place? |  | Please place the top of the footings 12" below grade. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Structural Engineers |  | 11/04/2020 |  |  |  |  | Closed | 11/11/2020 | 11/19/2020 | 11/12/2020 | 11/09/2020 | 11/04/2020
785 |  | 0 |  |  | Request for Information | Backing on 3rd & 5th Floor | Couple of backing questions: Backing clarifications for the sealing room mirrors. (See the attachemnt) Plywood infill in the hallways for the access doors to be replaced with 5/8" or 1/4" gyp to create 1/4" to 1/8" reveal for plaster. |  | This was confirmed per site visit on 11-4 with Creg Norton. |  |  | High | Creg Norton | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/04/2020 |  |  |  |  | Closed | 11/07/2020 | 11/09/2020 | 11/06/2020 |  | 11/04/2020
786 |  | 0 |  |  | Request for Information | East Tower Basement Beams | Is it necessary to galvanize the beams in the East tower Beams? This can cut down on approximately 10 days of time before installation. |  | Galvanizing of the beams in this area isn't critical as it is out of the way of direct water potential from the font. However, this decision to not galvanized should be brought up with the arch and owner for direction. We assume a credit would be provided back to the owner if these beams are not galvanized. ¦ Baptistry crawlspace and east tower steel beams/ horizonal assembly will be fireproofed and do not need to be galvanized or painted. Please refer to CCD 131 that was just sent out indicating the Baptistry crawlspace finishes. ¦ ¦ Scott/Kyle/Jeff, Please provide some input on changing the structural steel in the Basement needs to be galvanized or if it can be simple steel with the red iron steel paint? |  |  | Medium | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 11/06/2020 |  |  |  |  | Closed | 11/12/2020 | 02/23/2021 | 02/18/2021 | 11/19/2020 | 11/06/2020
787 |  | 0 |  |  | Request for Information | East Tower Floor boxes level 2,3,4,5 | With all of the additional plaster having to be removed or cut into in the East Tower rooms floors 2,3,4,5, we propose replacing the floor boxes with flush mounted wall boxes channeled into the plaster which will make them much better to access as discussed with Scott Hardy and Kyle Welch on 10/05/2020. Also there are 4 locations on the 4th floor at the rostrums at both ends of the priesthood room that would be better suited with floor boxes because the walls are solid wood and would not accommodate a flush mount box.(see attachments please advise) |  | We have no issue with the changes noted in this RFI as long as Architect approves of the changes. ¦ After further review and with the new floors being open and exposed, CRSA would like to keep the floor box outlets in the east rooms the way they are shown in the construction drawings. Floor boxes at the rostrum are acceptable. Place floor boxes at rostrum where they are out of traffic areas and out of the way as much as possible while sitting. ¦ ¦ Please review and advise if you concur with the adjustments outlined in this RFI. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/06/2020 |  |  |  |  | Closed | 11/13/2020 | 11/16/2020 | 11/13/2020 | 11/10/2020 | 11/06/2020
788 |  | 0 |  |  | Request for Information | Duct Openings in Floor - East Tower Basement | We have been able to pull all applicable dimensions for the beams added to the level 0.5 in the East Tower and, as we are preparing shop drawings, we are noting floor openings that need to be coordinated. Please see attached sketch with openings clouded. The green clouds appear to show floor openings, but these areas are hallways that require foot traffic. Are these openings required? If so - what is the size requirement? There are 2 clouds in blue that appear to be for duct passage (1 appears to be a wall plenum, the other appears to be a duct "closet"). Please provide size requirement for these as well. | Please provide direction that the concrete on deck is to pass through what appears to be block outs on the structural plans. | Those areas marked has concrete floors covering them. They are meant to indicate a horizontal penetration through the wall and not a vertical penetration up through the floor. ¦ |  |  | Medium | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 11/07/2020 |  |  |  |  | Closed | 11/14/2020 | 11/19/2020 | 11/12/2020 | 11/10/2020 | 11/07/2020
789 |  | 0 |  |  | Request for Information | Exit light elevations | we need an elevation for bottom of exit lights in relation to trim work around doors this would probably need to be a dimension from the largest trim so all of the exit lights would be the same elevation and not staggered. Also we would need some direction for nontypical doors such as arched openings etc. (please advise) |  | Please refer to ASI #67- Exit Signage Dimensions. ¦ ¦ Kyle per our email conversation you were working through this one on site. I will leave it up to you to determine the final mounting heights in relation to the finished trims, etc. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/09/2020 |  |  |  |  | Closed | 11/16/2020 | 12/08/2020 | 12/08/2020 | 11/19/2020 | 11/09/2020
790 |  | 0 |  |  | Request for Information | Wood Base Historical Bldg | CCD40R1 Item A, General note states Historical Bldg. has wood base type C2 or C3, however Finish Schedule states rm 060, 061, 062, 063, 064, 065, 066, 067, 067B, 067C, 068, to be base type C1 which is stone with wood trim on top and stair 3 to be C4 stone base with wood trim on top. Please clarify which is correct the General note wood base or finish schedule stone base with wood trim on top. |  | All of these bases shall be a wood base. We will update our finish schedule in 040r.2 reflecting this. See attached Response. ¦ See previous comment November 2020 ¦ ¦ We will leave this open until the updated CCD040 R2 is issued. |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 11/09/2020 |  |  |  |  | Closed | 11/16/2020 | 12/17/2020 | 12/11/2020 | 11/09/2020 | 11/09/2020
791 |  | 0 |  | 4/S211, 4/P401 | Request for Information | House Keeping Pad for Font Equipment | Please advise if housekeeping pads are wanted for font equipment FF-1 and UVF-1 and if typical detail 4/S211 is to be followed. Since font filter UVF-1 is owner provided (note 4/P401), please provide the cut sheet for this equipment or the size of pad to be provided. |  | See attached response from VBFA. Yes, provide a housekeeping pad for the font skid and pump per the attached dimensions. A pad is not required for the UV filter because it comes on its own stand. ¦ ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/10/2020 |  |  |  |  | Closed | 11/17/2020 | 12/17/2020 | 12/16/2020 | 11/17/2020 | 11/10/2020
793 |  | 0 |  |  | Request for Information | Dedication Lines for Data and AV | In past temples that Westland has completed there has been some Conduit/Raceways for Data and AV installed for dedication purposes. We can’t find anything on the drawings and would appreciate some direction on this. With us doing the wall rough ins right now it would be a good time for this to be installed. Otherwise this temp system will prove to be much more difficult to install in the future. |  | DS and DE box location and conduit requirements are located in the XE - Av sheets in the drawings. Refer to theses sheets for locations and requirements. ¦ see coment ¦ Will you please review the XE and AV drawings and let me know if you can find any COMM lines that mention being used for the dedication. I checked and I couldn’t see them. Thanks, |  |  | Medium | David Adams | Westland Construction, Inc. | Trask Johnson | Wilkinson Electric Inc | 11/10/2020 |  |  |  |  | Closed | 11/17/2020 | 11/16/2020 | 11/16/2020 | 11/12/2020 | 11/10/2020
794 |  | 0 |  | AD125, AE4508 | Request for Information | East Stair Tower Ceilings | Per direction given on AD 125 the stair tower ceilings have been removed but the drawings haven't been updated to show the reinstall (unless I'm missing it). 1. These ceilings have been removed to allow for the mechanical and structural upgrades above the ceiling. Please provide the ceiling height for reinstall and how it is to be constructed. Marked on attached drawings. 2. Please adjust note 2.64 on sheet AE4508 to show the ceiling has been removed and will need to be reinstalled. Marked on attached drawings. |  | Dave, this was already done in CCD 15 - (Gyp. plaster ceiling at historic) that was sent back in February. Let me know if you can find it or have any additional questions. ¦ Please see ASI #59 showing the added keynote on sheet AE4508. CCD 50 does supersede CCD 15. Ceilings at the 5th floor stairs shall be 8'-11" high. ¦ I see it now sorry about that. Will you please confirm that CCD #50 showing the ceiling height 8’-11” and ceiling type C2 supersedes CCD #15 showing the ceiling height 14’-5” and ceiling type C6. If you would change note 2.64 on sheet AE4508 to read that the ceiling is going to be removed it would be appreciated. |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/11/2020 |  |  |  |  | Closed | 11/17/2020 | 11/16/2020 | 11/16/2020 |  | 11/11/2020
795 |  | 0 |  |  | Request for Information | South wall shop 042 | Does the south wall of shop 042 fur out? there are several electrical devices between the upper and lower cabinets that would need to be fed horizontally across wall if surface mount. (please advise see attachment) |  | Please refer to CCD 114- Wall furring change. ¦ ¦ This item is asking about the wall finish along the south wall of the shop. We have devices mounted above the counter in this area that will need to be surface mounted with surface mounted conduit if the wall is not to be fur out. Please advise. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/11/2020 |  |  |  |  | Closed | 11/18/2020 | 12/08/2020 | 12/04/2020 | 11/12/2020 | 11/11/2020
796 |  | 0 |  |  | Request for Information | Intercom Door 125A | could we be provided with info. (shop drawings, cut sheets) for owner furnished intercom/camera at door 125A we will need backbox that will be mounted 48" to center per. reviewed precast penetrations. (please advise see attachment) |  | See Jessica Blundell's comment below for a response to this RFI. ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Trye Hatch | ENVISION ENGINEERING | 11/11/2020 |  |  |  |  | Closed | 11/18/2020 | 11/18/2020 | 11/17/2020 | 11/16/2020 | 11/11/2020
797 |  | 0 | 230000 | P401 | Request for Information | Piping serving Laundry Steam Boiler | Drawing P401, detail 5 indicates low pressure steam(LPS), condensate(D) and vacuum (V) to serve the Steam Boiler (SB-1) and the owner provided steam press and spotting board. Specifications and/or piping schedule provided within the contract drawings do not appear to provide material type for the above listed piping systems. | Please provide a specification and/or piping schedule indicating required material for the LPS, D and V piping systems. | Provide the following materials for the piping connected to the laundry steam boiler: • Low-Pressure Steam - Schedule 40 black steel pipe • Condensate - Schedule 80 black steel pipe • Vacuum - 304 stainless steel tubes conforming to ASTM A312/A312M or ASTM A790/A790M and rated for 2000 PSI or greater. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/11/2020 |  |  |  |  | Closed | 11/26/2020 | 12/16/2020 | 12/15/2020 | 11/12/2020 | 11/11/2020
798 |  | 0 |  |  | Request for Information | East Site Lighting | There are a group of bollard light at the east fountain/plaza that don't have a circuit or relay callout (see attachment please advise), as well as two that are adjacent to the East of the Historical Temple? |  | The bollards referenced are circuited together to Panel H2L1-23 and Relay Panel LCPA1-5. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 11/11/2020 |  |  |  |  | Closed | 11/18/2020 | 11/18/2020 | 11/16/2020 | 11/12/2020 | 11/11/2020
799 |  | 0 |  |  | Request for Information | Monument elevations | Provide monument sign elevations for the column and wall section for the concrete footing, grade skirt, of top of concrete |  | See attached detail for updated dimensions. ¦ ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Zac Givens | Westland Construction, Inc. | 11/12/2020 |  |  |  |  | Closed | 11/15/2020 | 11/13/2020 | 11/12/2020 | 11/12/2020 | 11/12/2020
800 |  | 0 |  |  | Request for Information | Crawlspace Finishes | Finish schedule does not included Historic crawlspace, brides corridor crawlspace, east tower crawlspace, west tower crawlspace. Is epoxy coated flooring or any other type of finishes required in these spaces? |  | See CCD 131 for finish instructions. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/12/2020 |  |  |  |  | Closed | 11/19/2020 | 02/19/2021 | 02/18/2021 | 11/12/2020 | 11/12/2020
801 |  | 0 |  |  | Request for Information | CCD 104 Door Hardware Revisions | There are multiple Doors with electrified hardware IE. Surf. Auto Operator, Actuator wall mount, Electric Hinge, Panic W/ Alarm ETC. we need to be provided circuitry for the operators and Door specific Details for rough in. We need Answers for the Annex Basement Doors ASAP Drywall is scheduled for early December (please advise) |  | I just got a peace hardware schedule from the Hardware supplier. Please review and let me need anything else. ¦ I have reviewed this and found that it is missing sheet EP100B which would add power for the ADA operator for door 060B, it was originally a pneumatic operator with an air compressor in the baptistry crawl space which has been removed in this CCD on page 15 EP100A the architectural drawings show this door having an ADA operator. ¦ See attached sheet EP100B with power changes for ADA door. ¦ Per Trask - I have reviewed this and found that it is missing sheet EP100B which would add power for the ADA operator for door 060B, it was originally a pneumatic operator with an air compressor in the baptistry crawl space which has been removed in this CCD on page 15 EP100A the architectural drawings show this door having an ADA operator. ¦ David, the submittal attached only has part and catalog numbers we will need actual shop drawings of each door and how they rough in |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 11/16/2020 |  |  |  |  | Closed | 11/23/2020 | 12/08/2020 | 12/03/2020 | 12/03/2020 | 11/16/2020
802 |  | 0 |  |  | Request for Information | confirming outlet deletion | Confirming that as per OAC on 11/12/2020 we are directed to delete exterior GFCI outlet north of dock door (see attachment) |  | Envision is OK with removing this outlet. ¦ ¦ ¦ Please provide any further information given by Brian, so this item can be resolved. ¦ Yesterday 11/18 we were asked about relocating said outlet we gave some suggestions to Brian Chandler about where it could be relocated and are waiting further direction |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Trask Johnson | Wilkinson Electric Inc | 11/16/2020 |  |  |  |  | Closed | 11/23/2020 | 12/21/2020 | 11/19/2020 | 12/01/2020 | 11/16/2020
803 |  | 0 |  |  | Request for Information | Planter footings | Per page LL501 hardscape details. Confirm the detail # 8 is suppose to be labeled as detail #7. The same detail is lacking stabilizing connections and footings. The concern is that the 4" curb wall will be unstable and unsecure. Possible solutions pour a footing for the 4" curb wall Pour the 4" curb monolythicly In addition to pouring additional concrete is there a dowel needed to secure the curb to the sidewalk |  | See attached sheet for revised detail 7 per field discussion. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 11/17/2020 |  |  |  |  | Closed | 11/24/2020 | 12/03/2020 | 12/03/2020 | 11/18/2020 | 11/17/2020
804 |  | 0 |  |  | Request for Information | EIFS Instead of Plaster on Annex | Please confirm that we are to install an EIFS system instead of the Plaster systems on all of the clear story walls, the North upper entry and return walls. EIFS submittals forthcoming. |  | As was discussed on 11-16-2020 EIFS to be used in lieu of stucco plaster system. this for the areas mentioned in the RFI. Sub-Contractor to provide any cost savings or schedules benefits to general contractor. |  |  | High | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 11/17/2020 |  |  |  |  | Closed | 11/20/2020 | 11/18/2020 | 11/17/2020 |  | 11/17/2020
805 |  | 0 |  |  | Request for Information | 4th floor speaker wire path confirming RFI | Per conversation and job walk-through with Brad Justensen with the church A/V department, it was decided to run the speaker wiring to the speakers in the lowered ceilings of the main room of the 4th floor. 4" square boxes are able to be roughed in the ceiling within 1' or less from the speakers, so minimal wiring would be visible. This is a much shorter and more viable path, and it allows better mounting of the speakers' support brackets. (See attached drawing) Please confirm that we are good to move ahead with the installation according to this method. |  | Follow direction per Brad, verify that all conduit in ceiling is concealed with the exception of the cable from box to speaker. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 11/17/2020 |  |  |  |  | Closed | 11/24/2020 | 11/19/2020 | 11/19/2020 | 11/18/2020 | 11/17/2020
806 |  | 0 | 230000 | M101, M603, M502 | Request for Information | CD-7 Plenum | Drawing M101, Foyer 103, waiting 105, 109, hall 106, chapel 110, and instruction 111 calls for installation of HVAC register CD-7 to include plenums. Drawing M603 air device schedule for CD-7 refers to drawing M502, detail 4 indicating a plenum for CD-7 to be 20" tall plenum. The approved manufacturer for the CD-7 register is Titus. Titus only makes the plenum in 18" tall size. | Please confirm that the manufactured plenum size of 18" tall is acceptable. | The 18" tall plenums from the manufacturer are acceptable for the diffusers serving Foyer [103], Waiting [105], and Hall [106]. The plenums for the supply diffusers serving Waiting [109], Chapel [110], and Instruction 1 [111] may also be 18" but will need to be customized for the 18/8 rectangular duct connections as shown on the drawings. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/19/2020 |  |  |  |  | Closed | 11/21/2020 | 11/30/2020 | 11/20/2020 | 11/19/2020 | 11/19/2020
807 |  | 0 |  |  | Request for Information | Hedge curb | Per field discussion 11.18.20 please confirm the concrete curbs around the east plaza hedges are not needed and are to be removed. |  | Correct, the curbs are no longer needed. Take care during removal to avoid damage to the hedges or roots. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 12/03/2020 | 11/24/2020 | 11/19/2020 | 11/19/2020
808 |  | 0 |  |  | Request for Information | Removal of the two Mimosa tree's | Please confirm, the two mimosa tree's in area A are to be removed only. The redbud trees will not be planted in their place anymore. |  | This is correct. After reviewing the site with the Owner's Landscape Architect it was decided there is sufficient shade and would prefer to have the Mimosa trees removed and not replaced. The Redbud that is currently in the holding area may be used elsewhere on the site where Redbud's are being called for, such as the Visitor's Center, East Plaza, or Bride's Exit Plaza. The attached PDFs now include the removal of these trees from the planting plan. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 12/03/2020 | 11/19/2020 | 11/19/2020 | 11/19/2020
809 |  | 0 | 230000 | AE 125 | Request for Information | Historic Spiral Stair-Ceiling Layout | Drawing AE125, North and South spiral staircase, above ceiling layout includes lights and HVAC fan coils. Dimensions for locations to install these are not provided. | Please provide dimensions for layout of lights and HVAC equipment at these ceiling locations. | Please refer to ASI #69. Thanks. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 12/07/2020 | 12/04/2020 | 11/19/2020 | 11/19/2020
810 |  | 0 | 230000 | MP100 | Request for Information | Font Skid heating water supply and return piping | Drawing MP100, font skid package, during the design changes moving the font skid from the Annex to the Historic and then back to the Annex Bldg, it appears that the heating water supply and return piping serving the font skid heat exchanger have been omitted. See attached screen shot of the font equipment room for the approximate location of the 2" heating hot water taps that appear to have been omitted. | Please confirm that it is acceptable to connect to the 6" main hot water piping with 2" supply and return to serve the font skid package heat exchanger. | The proposed solution is acceptable. An alternative would be to connect the piping to the 3" heating water pipes that route directly above the font equipment and continue on to the historic temple crawlspace. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 11/30/2020 | 11/23/2020 | 11/19/2020 | 11/19/2020
811 |  | 0 |  |  | Request for Information | Vanity light placement dimensions | Please provide placement dimensions for vanity lights in the following rooms 016, 026, 027 and 048 we also need a outlet location in room 017 (see attachment) |  | See ASI #70 for response. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 12/10/2020 | 12/08/2020 | 11/19/2020 | 11/19/2020
812 |  | 0 | 220000 | P110B | Request for Information | Dewatering sump-Vent | Drawing P110B, Room 021, dewatering sump. It appears there is a missing vent line that needs to serve this sump. See attached. | Is it acceptable to tie the sump vent into the existing 3" vent located in the adjacent mechanical room? Note that both sumps located in room 020A have 2" vents serving them. | The proposed vent line is acceptable as long as the routing avoids running above any electrical panels in East Mechanical [020A]. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/19/2020 |  |  |  |  | Closed | 11/26/2020 | 12/02/2020 | 12/01/2020 | 11/20/2020 | 11/19/2020
813 |  | 0 |  |  | Request for Information | CCD 104 Hardware Finishes | Please confirm hardware finishes. Transmittal letter for custom hardware 087100-2 reference a two tone and different finishes per location. All Hardware in CCD 104, with exception of the basement, call for the hardware to be a dark bronze. |  | Door hardware finish locations were provided via a color coded floor plan, and sent to CRSA a few weeks ago. Locations were decided from a team meeting. ¦ Door Hardware Finish was added to the door schedules in CCD 101R.1 ¦ ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/20/2020 |  |  |  |  | Closed | 11/27/2020 | 01/25/2021 | 01/20/2021 | 01/06/2021 | 11/20/2020
814 |  | 0 |  |  | Request for Information | Wall Vinyl 2 Manufacture TBD - CCD_40R1 | CCD_40R1 added a Wall Vinyl Type 2 without a manufacturer. Please provide manufacturer information for WV2 as soon as possible to mitigate lead time concerns. |  | See ASI 114. WV2 has been omitted. All locations with Wall Vinyl will get WV1. WV1 has been updated as well. |  |  | Medium | Camron Walker | Westland Construction, Inc. | Interior Designer |  | 11/20/2020 |  |  |  |  | Closed | 12/04/2020 | 03/23/2021 | 03/19/2021 |  | 11/20/2020
815 |  | 0 |  | EC103 | Request for Information | 3rd floor sealing room floor WAP relocate or eliminate. | We have been informed by Scott Hardy and others that the ceiling mounted Wireless Access Point (WAP) shown (and already installed) in the 3rd floor sealing room 4, room 318 ceiling will not be desirable as it will be highly visible and obtrusive. Should we relocate it or simply eliminate it? |  | It has been determined that the ceiling mount WAP in this room will be removed and replaced with a wall mounted device at outlet height. Revised drawings will be issued as part of CCD-118 to reflect this change. ¦ See comment from Jessica with Envision Engineering. |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 11/23/2020 |  |  |  |  | Closed | 12/03/2020 | 02/09/2021 | 02/05/2021 | 11/23/2020 | 11/23/2020
816 |  | 0 |  |  | Request for Information | Brass deco lighting overall heights | What are the requested overall heights for all hanging ceiling fixtures? All type A Chandeliers, type G pendant, type I pendant. Gloria Hayley ID and team have an existing spreadsheet that needs to be filled out. Thank you! |  | this information was provided in ASI 76R.2 and 76R.3. ¦ ¦ Hi Scott, There are still heights that are missing. See attached. Thank you, Leeann | Interior Designer |  | Medium | Leeann Latsch | Remains Lighting | Interior Designer |  | 11/23/2020 |  |  |  |  | Responded | 11/30/2020 |  | 03/31/2021 | 11/24/2020 | 11/23/2020
817 |  | 0 |  |  | Request for Information | Visitor Center sod irrigation | Per CCD 088 on sheet LI 109 note stating to use the existing irrigation to remain to irrigate the sod areas in front of the VC and park strip. Provide details for valves that control the irrigation for these sod areas. |  | Please see our attached comments to this RFI ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 11/24/2020 |  |  |  |  | Closed | 12/06/2020 | 12/03/2020 | 12/02/2020 | 11/24/2020 | 11/24/2020
818 |  | 0 |  |  | Request for Information | Ceilings in Spiral Stair Shafts | The existing ceiling support structure in both the north and south side of the east tower and need to be removed and replaced to accommodate the HVAC and other BIM needs. With the preexisting supports in the way, and moving the piping and HVAC is not an option. With removing the preexisting ceiling structure and replacing it as we did for the floors, should help to improve the in integrity of the stairs. Please change Note C6 on sheet AE123 to indicate that the Ceiling is to be reframed and reinstalled. For reference I have included a sheet showing how the ducts are going to be installed in the shafts. |  | This was RFI was discussed with CRSA. It was agreed that they would provide an answer to this RFI. ¦ Ceilings and historic bracing at center chase in the stair towers can be removed and replaced under the existing floor joists to provide HVAC the required access to be accessible. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/24/2020 |  |  |  |  | Closed | 11/27/2020 | 12/08/2020 | 12/04/2020 |  | 11/24/2020
819 |  | 0 |  |  | Request for Information | HVAC Crawl Space at Spiral Stairs | Please confirm the W14x30 below the conformation rooms running North/South can shift to the East as indicated in the attached. Also, that the W14x30 at the heading from the conformation room into the Spiral stair crawl space can be eliminated. Please provide a post install embed detail. | Conformation | This is acceptable. Please ensure that the beam is moved so it is no further than 11'-0" from the furthest stone wall. See attached sketch for connection plate information ¦ |  |  | High | Jason Fullmer | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 11/25/2020 |  |  |  |  | Closed | 11/27/2020 | 11/30/2020 | 11/25/2020 | 11/25/2020 | 11/25/2020
820 |  | 0 |  |  | Request for Information | Missing Ledger Embeds | There are no embeds for the metal decking ledger angle in this location. The shop drawings from Glassey don’t show any. The two edited drawings with the red line are the locations of the needed embed and decking ledger. Will has asked if we can use a section of ledger angle with a ¾ titan anchor every 4 feet on center. |  | Attached the ledger angle to the wall using a 3/4" x 8-1/2" Simpson Titen HD screw anchor spaced at 18"o.c. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 11/25/2020 |  |  |  |  | Closed | 11/27/2020 | 12/01/2020 | 11/25/2020 |  | 11/25/2020
821 |  | 0 |  |  | Request for Information | Custom Hardware Adjustments | We’re not able to relocate the lever to 3-1/2” above the bottom of the plate as the cylinder will come into contact with the bead detail. I’ve located the lever 3-1/4” from the bottom instead. If you need the 3-1/2” spacing, we can increase the overall height of the escutcheon to make room for the cylinder. Let me know which route you’d like to take. For reference we have attached some shop drawings showing how the hardware will appear. |  | The 3-1/4" dimension is acceptable. This was also reviewed and approved in the shop drawings. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/25/2020 |  |  |  |  | Closed | 12/01/2020 | 12/17/2020 | 12/16/2020 | 12/09/2020 | 11/25/2020
822 |  | 0 |  |  | Request for Information | CCD104 Door Actuator locations | We need locations of door actuators for doors associated with CCD104 Door# 003A, 006A, 019, 028, 028A, 033B and 125 (this may not be all of them) We also need circuiting information from Envision |  | These changes were issued by Envision as part of CCD-095R.1. CRSA should be sending those revised drawings to contractor. ¦ See response sent by Jessica Blundell on 12-21-20 ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Scott Hardy | ENVISION ENGINEERING | 11/25/2020 |  |  |  |  | Closed | 12/02/2020 | 01/07/2021 | 01/07/2021 | 11/25/2020 | 11/25/2020
823 |  | 0 |  | XE530 | Request for Information | T-stat and Clock Display Mounting Heights | Please see the attached drawings/cutsheets for the T-stats and clock displays. XE530 calls for Clock Display to be mounted at 66" AFF on center and RFI 426 calls for the T-stats to be mounted at 60" AFF on center. The attached clock display detail is from Church AV and shows a slightly large clock display than on XE530. In order to provide spacing between the Clock Display and T-stat devices, please advise if it is acceptable to mount the clock display at 68" AFF on center. This would allow for a 2-11/16" gap between the two. Please advise. |  | Envision is OK with the new mounting height. Verify with owner that this mounting height is acceptable. ¦ These heights are acceptable. Please proceed. ¦ ¦ |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/28/2020 | XE530 |  |  |  | Closed | 12/01/2020 | 12/17/2020 | 12/14/2020 | 12/10/2020 | 11/28/2020
824 |  | 0 |  | AE4317, AE4202, AE4302, AE4402, and AE4502 | Request for Information | West Stair Tower RR and Lobby RCPs | The RCP's for the west stair tower lobby's and restrooms on levels 1 through 5 appear to vary from floor to floor and some have conflicts in the layout. Reference sheets AE4317, AE4202, AE4302, AE4402, and AE4502. Please clarify layout where clashes exist and advise if a standard layout is wanted from floor to floor. If so, please provide standard layout. |  | See the attached for ASI #72 in response to ceiling clarification ¦ ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | David Adams | Westland Construction, Inc. | 11/28/2020 |  |  |  |  | Closed | 12/05/2020 | 12/22/2020 | 12/18/2020 | 12/21/2020 | 11/28/2020
825 |  | 0 |  |  | Request for Information | Annex 1st Floor Missing Panel and Circuit Designation | Please advise as to the circuit and panel(s) the clouded outlets are to be ran on the attached page. |  | See attached EP101 sheet with missing circuit and relay information turned on. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 11/30/2020 |  |  |  |  | Closed | 12/07/2020 | 12/03/2020 | 12/02/2020 | 11/30/2020 | 11/30/2020
826 |  | 0 | 230000 | M100B, M409 | Request for Information | CCD#098-Return Duct Risers | Per CCD#098 direction, drawing M100B, along gridline HF at laundry 055 and 056, return duct riser is shown to be 60x20. Drawing M409 indicates this same return duct riser as 60x24. | Please advise which size is correct for the return duct risers. | 60/24 is preferred but 60/20 is acceptable if needed to pass between the west stone wall and the east walls of the chases at the back of Instruction A-3 [210] on level 2. If a reduction in size is needed, maintain 60/24 to the floor of level 2 and then neck down to 60/20 to pass from level 2 to the ceiling of level 0.5. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 11/30/2020 |  |  |  |  | Closed | 12/07/2020 | 12/02/2020 | 11/30/2020 | 11/30/2020 | 11/30/2020
827 |  | 0 |  |  | Request for Information | CCD 095 Missing Wall Types | Please provide the wall types and dimensions for the wall that where adjusted on Level 0.5 in CCD 095. For reference I have attached a snip from the drawings indicating the walls in question. |  | Please refer to CCD #100 for wall type and dimensions. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 11/30/2020 |  |  |  |  | Closed | 12/04/2020 | 12/02/2020 | 12/01/2020 |  | 11/30/2020
828 |  | 0 |  |  | Request for Information | Lighting control panels circuit relocation- Historic Temple | Can some of the Lighting Control circuits in the Historic Temple be changed to originate from different Lighting Control Panels, and in some cases different Panelboards? This would accomplish the following things: 1- It almost always simplifies the conduit runs and creates fewer of them. 2- It simplifies troubleshooting down the road. 3- Per Rusty Hughes with Lyle W. Williams, having a room, hall, or common area be fed from one Lighting Control Panel (LCP) makes it so "the system runs a little quicker (response time) and there are less chances for errors...the more we minimize having to switch over the network the better the system is." 4- It simplifies programming of the LCP's, which is beneficial to both the programmer and the end user. | Make the adjustments to the lighting control circuits in the Historic Temple as noted in the attachments. The proposed changes as to which LCP certain circuits are fed from in the Historic temple will modify the circuit/solenoid counts in the LCP’s as follows: LCP-T5 +2 LCP-L3 +3 LCP-T3 -4 LCP-T3B -2 LCP-T1 +1 | The lighting control changes have been addressed on the phone call on 12/2 and also in the issued drawings ASI-071. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 12/01/2020 |  |  |  |  | Closed | 12/08/2020 | 12/17/2020 | 12/10/2020 | 12/01/2020 | 12/01/2020
829 |  | 0 |  |  | Request for Information | AV room 202 emergency circuit changes | Can we feed 3 circuits in AV room 202 from Panel L3E3 - 10, 12, 14 instead of LE - 13, 15, and L2E1 - 5? | Feed these dedicated, emergency circuits from L3E3. Originally L3E3 only provided 12 breaker spaces which would have been insufficient, however an SPD was specified for the panelboard which required that spaces be added. L3E3 now provides at least 18 (and possibly 24+) breaker spaces. The load incurred by adding these 3 circuits is negligible; 1 Amp or less per circuit. This will shorten conduit and wire runs significantly, and will keep the circuits fed from a nearby panel instead of multiple panels scattered throughout the temple addition, making maintenance and troubleshooting easier. Please see attachment. | Since panel L3E3 now has available space and as long as it will not overload the upstream panel, we see no issue with changing these circuits. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 12/01/2020 |  |  |  |  | Closed | 12/08/2020 | 12/03/2020 | 12/02/2020 | 12/01/2020 | 12/01/2020
830 |  | 0 |  |  | Request for Information | Monument sign lettering | Please supply information for carved lettering |  | See attached for updated detail on the sign lettering. Additional information will need to come from the Owner. ¦ See response from Greg B. ¦ Information has been provided by the owner in ASI #099. See attached drawing dated 03/05/2021 ¦ Generally this is something that needs to be requested from the Owner. ¦ ¦ ¦ In the past I have had to go through the Architect in order to get the font type from the Church. Is that not the case on this one? |  |  | High | Bob Durrant | IMS Masonry Inc. | CRSA ARCHITECTURE |  | 12/02/2020 |  |  |  |  | Closed | 12/13/2020 | 03/10/2021 | 03/08/2021 | 12/08/2020 | 12/02/2020
831 |  | 0 |  |  | Request for Information | EAST & NORTH FOUNTAINS: PRODUCTION DWGS REVISED 01-DEC-20 | Please review the revised production drawings for the NORTH & EAST Temple Fountains |  | Mark, Will you please submit this as a submittal. If you are not sure how to do it please reach out to me 801-372-1574 or Camron Walker 801.875.2600. Thanks ¦ Hi David: As it turns out the zipped .DXF file is only 14 MB so you should receive this … I will call to confirm with you. I will send the NORTH fountain files in a moment. Thanks David, Mark Gabriele Artisan Granite, LLC 20 Azalea Court East Greenwich, RI 02818 Phone/SMS: (401) 219-1521 Web Address: www.artisangranite.com |  |  | Medium | Mark Gabriele | Artisan Granite, LLC | Westland PE’s |  | 12/02/2020 |  |  |  |  | Closed | 12/09/2020 | 12/10/2020 | 12/08/2020 |  | 12/02/2020
832 |  | 0 |  | Similar to C1/AE527 | Request for Information | 3RD FLOOR BASE FINISH | On the 3rd floor in the instruction rooms and corridors, 3/4" plywood is currently installed at the bottom of walls as backing for the baseboards. Thickness of the drywall is 5/8". That leaves a 1/8" difference between the drywall and the plywood. If plywood is left as is, there will be a gap between the baseboard and the finished drywall. Please advise how to proceed with install of 5/8" drywall. | Plywood be installed within the cavity of the walls and sheet rock run down to the floor. | Please install the 5/8” Drywall as shown in the project documents and float the 1/8” gap at the base board backing to the drywall. The backing was installed in a way that allows for it to be used as a guide for the wall plain. ¦ This is not what is shown in the project documents. The project documents show drywall running to the floor. |  |  | High | Aaron Bowers | Pete King Commercial | Westland PE’s |  | 12/02/2020 |  |  |  |  | Closed | 12/10/2020 | 12/10/2020 | 12/08/2020 |  | 12/02/2020
833 |  | 0 | 230000 | M103, S104 | Request for Information | Equipment V-3-18 and V-3-19B duct design proposed change | Drawing M103, ducts serving equipment V-3-18 and V-3-19B are shown routing up through the lattice trusses and some of the floor joist spaces just below level 4. Drawing S104 indicates new W14 beams at the same location of the ductwork on either side of the lattice trusses. Due to the size of these new steel beams it appears we cannot route some of the duct per plan. U.S. Mechanical has split these ducts and changed routing as needed to get them up through the joist. | See attached proposed duct split and routing drawings for review and approval. Please confirm that this design intent is acceptable. | The proposed ductwork routing adjustments are acceptable. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/03/2020 |  |  |  |  | Closed | 12/13/2020 | 12/16/2020 | 12/15/2020 | 12/04/2020 | 12/03/2020
834 |  | 0 |  |  | Request for Information | Stair-5 Handrail Molding Conflict | Please advise if this cantilevered portion (attached) of the floor can be cantilevered Further to the North to allow for the handrail to land on a flat section of wall adjacent to the door trim. |  | This is acceptable structurally. Please coord also with architect. ¦ See response from ARW. Cantilever floor and adjust railing out an additional 6" for railing to clear casework at opening. ¦ |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/04/2020 |  |  |  |  | Closed | 12/06/2020 | 12/10/2020 | 12/10/2020 | 12/08/2020 | 12/04/2020
835 |  | 0 | 220719 | P sheets | Request for Information | Domestic Plumbing Piping Insulation | Insulation specification 220719-16, paragraph 3.10, part A 1, 2 and B 1, 2, schedule indicates pipe insulation wall thickness for copper pipe conducting domestic hot and cold water to be 1 1/2". CCD# 29R3 changed the domestic water piping to NUPI Niron product which carries a higher R value insulating property than copper. Due to the higher R value and the challenges to penetrate historic walls and conforming to space constraints for all piping, we would like to propose using 1" wall thickness on larger diameter domestic water piping and 1/2" wall thickness on smaller diameter piping. | Please review the NUPI Niron R value and provide an insulation schedule indicating what wall thickness will be allowed for domestic piping insulation. | Please provide pipe insulation thicknesses as described in the project specifications. Per tables 6.8.3-1 and 6.8.3-2 in ASHRAE 90.1-2016, the insulation thicknesses for non-metallic pipe may only be reduced for pipes with walls thicker than schedule 80 pipe. The Nupi Niron piping being installed is thinner than schedule 80 pipe and therefore must conform to the prescribed insulation thicknesses indicated in these tables. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/07/2020 |  |  |  |  | Closed | 12/13/2020 | 12/16/2020 | 12/15/2020 | 12/08/2020 | 12/07/2020
836 |  | 0 | 230000 | M101, M502, AE582 | Request for Information | CD-7 Plenum allowed width | Drawing M101, rooms 103, 105, 106, 109, 110 and 111, indicates installation of CD-7 plenums at the millwork. Drawing M502, detail 4 indicates the plenum to be 5" in width. See attached drawing for detail. Architectural drawing AE582 does not give a required plenum dimension. Following a discussion with the manfacturer, Titus only offers the plenum in a 5.75" wide dimension to accomadate the CD-7 linear diffuser registers. | Please advise if the 5.75" dimension fr the plenum will be acceptable for installation within the millwork as shown. | An additional 0.75" for the diffuser plenum would leave a material thickness of exactly 1" for the GFRG entablatures in the Annex. Coordinate the exact dimensions for the diffuser plenums with the fabricator for the GFRG entablatures in the Annex and verify that 1" will provide enough material to construct the entablatures. If additional material thickness is required for the GFRG entablatures then do at least one of the following: 1) Pull the diffusers closer to the wall while still leaving room for light fixtures on top of the entablatures. 2) Provide custom sheet metal plenums that will meet the 5" width shown in detail 4/M502. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/07/2020 |  |  |  |  | Closed | 12/10/2020 | 12/16/2020 | 12/15/2020 | 12/08/2020 | 12/07/2020
837 |  | 0 |  | CCD-044, sheets EL105A and EL105B. | Request for Information | Light Fixture Type WS-X | Sixteen type WS-X light fixtures were added in CCD-044. These were not added to the fixture schedule and being a "WS" (wall sconce) type light fixture I assumed these were provided by Remains. Who provides these, and what type of light is it? |  | The (16) Fixture Type: WS-X, Wall Sconces are located in the Attic Space above the Priesthood Room Ceiling so they are not being manufactured by Remains, and they shall be sourced by the Electrical Contractor. They shall be manufactured by, or equal to, a Leviton Manufacturing Co., Inc., Model No. 49875, Medium Base, Keyless Porcelain Lampholder. The Lamping for these Fixtures shall consist of: (1) Osram/Sylvania LED17A21/DIM/O/930/UB (78118) 17-Watt, 120-Volt, 3,000K, 92 CRI, 1,600-Lumen, 25,000-Hour A21 Frosted LED Bulb w/Medium (E26) Screw Base The complete specification for these fixtures shall be added to the Lighting Fixture Schedule and will then be issued with the next CCD. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 12/09/2020 |  |  |  |  | Closed | 12/16/2020 | 12/14/2020 | 12/14/2020 | 12/10/2020 | 12/09/2020
838 |  | 0 |  |  | Request for Information | Planter next to visitors center glass windows | On page LL108 it shows pavers next to the visitors center. CCD 088 now shows a planter with irrigation and plants. There is no detail called out for a footing for this planter. Is it just a rat slab or curb wall and does it need a footing? Please provide direction. Per CCD 088 page LL108 it shows paver detail M (LL514 detail #1) for the border and Paver detail N (LL514 #2) for the field. Please confirm this is correct. |  | That new planter will be an at-grade plant bed, no walls or curbs will be necessary. Refer to detail 5/LL501 for the transition between the pavers and the plant bed. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 12/09/2020 |  |  |  |  | Closed | 12/16/2020 | 12/21/2020 | 12/15/2020 | 12/10/2020 | 12/09/2020
839 |  | 0 |  |  | Request for Information | Winding Stair Ceiling Light and HVAC Conflict - ASI 69 | The lighting layout will need to be reconfigured there are multiple clashes with beams and mechanical access panels (See Attachment Please Advise) |  | Architect to coordinate lighting for each spiral stair. The fan coils at the top of each staircase will stay in roughly the same locations as currently indicated but may shift slightly as needed. Any needed adjustments to the fan coils will be coordinated in the field with Westland. ¦ ¦ We may need to coordinate this in a meeting onsite? |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 12/09/2020 |  |  |  |  | Closed | 12/13/2020 | 03/05/2021 | 02/16/2021 | 02/16/2021 | 12/09/2020
840 |  | 0 |  |  | Request for Information | Multiple VC questions | Per page LL203 in CCD 088 it shows a trash can by the sidewalk-paver corner. (PDF) 1. Does this need concrete to sit on? 2. Before a base is poured please confirm the desired location. Red, green, or yellow Red clouded area where the trench drain connects to the underground shows the pavers look like they are changing. Is this the case and if so, provide a detail for the pavers? Per page ES200 there is a Light bollard in the raised planter. (PDF) 1. Confirm this is the correct location of the bollard is to remain in the raised planter and the direction of the mow curb. There is no direction on how to treat some of the lose ends at the visitors center. (Pictures) 1. There is a bollard base next to the mechanical room door on the east side. Brian has expressed that it would be good to have light in that area. If this is to remain provide direction to connect it. 2. There is also an electrical outlet it is not called out to demo or reuse. Provide direction 3. Is it the desire that the visitors center site lighting be on the same automated system as the temple? If so, provide direction to accomplish this. 4. There are wires in conduit that have been disconnected from the site but are now exposed. Please provide direction. |  | See attached for responses. Electrical questions will be responded to separately by David Tibbitts. ¦ Per page LL203 in CCD 088 it shows a trash can by the sidewalk-paver corner. (PDF) 1. Does this need concrete to sit on? Greg Boudrero responded 2. Before a base is poured please confirm the desired location. Red, green, or yellow Greg Boudrero responded Red clouded area where the trench drain connects to the underground shows the pavers look like they are changing. Is this the case and if so, provide a detail for the pavers? Greg Boudrero responded Per page ES200 there is a Light bollard in the raised planter. (PDF) 1. Confirm this is the correct location of the bollard is to remain in the raised planter and the direction of the mow curb. The Bollard will be relocated as indicated by Greg Boudrero… this change will be issued as part of CCD 121 There is no direction on how to treat some of the loose ends at the visitors center. (Pictures) 1. There is a bollard base next to the mechanical room door on the east side. Brian has expressed that it would be good to have light in that area. If this is to remain provide direction to connect it. We do not know what the base was used for previously, but it isn’t a Bolted Bollard Base. We do not currently have a Bollard in this location, but we can add one there if the owner directs. If a Bollard is desired at this location please advise us ASAP so we can issue the change as part of CCD 121 2. There is also an electrical outlet it is not called out to demo or reuse. Provide direction. Please provide additional information. We will need to know more information about the specific locations of these items and where they are currently fed from and other details. 3. Is it the desire that the visitors center site lighting be on the same automated system as the temple? If so, provide direction to accomplish this. Please provide additional information. We will need to know more information about the specific locations of these items and where they are currently fed from and other details. 4. There are wires in conduit that have been disconnected from the site but are now exposed. Please provide direction. Please provide additional information. We will need to know more information about the specific locations of these items and where they are currently fed from and other details. We can do a phone call to discuss if needed. ¦ ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Electrical Engineers |  | 12/09/2020 |  |  |  |  | Closed | 12/17/2020 | 02/03/2021 | 01/21/2021 | 01/08/2021 | 12/09/2020
841 |  | 0 |  |  | Request for Information | Door operator Actuator elevations | CCD104R1 is showing an elevation of 2'8" to center of door actuators this is much lower than they are usually installed. electrical drawings have a detail showing actuators up to 48" to center this is the typical elevation we see. (see attachments please advise) |  | Install all door operator actuators buttons at 42" o.c. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 12/10/2020 |  |  |  |  | Closed | 12/13/2020 | 12/17/2020 | 12/15/2020 | 12/10/2020 | 12/10/2020
842 |  | 0 | 230000 | MP100A | Request for Information | Hydronic pipe at historic west stair tower wall | Drawing MP100A, sheet note 1 at west tower mechanical room indicates 3" hot water heating supply and return piping risers up to the upper levels. Note that this piping is to include 2" insulation which adds up to 7" in total diameter for each pipe. The drawings indicate this piping being installed within a 6" stud wall. | Please see attached drawing and markup. Please advise how to proceed with 7" pipe installation within a 6" wall. | I discussed this item with Scott Gilberg and Jeff Adams at CRSA. The walls in question will increase from 6" studs to 8" studs to accommodate the 3" HWS/HWR pipes with insulation. The walls will be updated in a forthcoming CCD from CRSA. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/10/2020 |  |  |  |  | Closed | 12/17/2020 | 12/17/2020 | 12/16/2020 | 12/10/2020 | 12/10/2020
843 |  | 0 |  |  | Request for Information | 200 east asphalt demo | Per CCD 088R1 page C.5 shows asphalt to be cut and removed on 200 east. Is the extant of asphalt cutting and removal determined by the purple shaded area (solid red line) or is it to follow the cut line (dashed red line)? |  | It is the cut line (dashed red line). See the attachment. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 12/10/2020 |  |  |  |  | Closed | 12/17/2020 | 12/21/2020 | 12/16/2020 | 12/10/2020 | 12/10/2020
844 |  | 0 |  | CCD-110, ES101 | Request for Information | Site Security Camera Cable Lengths | See attached, revised security camera drawing (CCD-111). Could we run cameras #8, 11, and 12 to the visitor's center to keep within 300'? Camera runs for #9 and 10 are longer than 300'. Please advise. |  | The church security/IT has confirmed that it is acceptable to feed these 3 cameras from the visitor center. ¦ Any cable lengths over 300' shall be fiber and have a fiber box on the pole, per detail 2/EC503. ¦ ¦ Camera runs #9 and #10 (east side) are longer than 300'. Please advise. |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 12/10/2020 |  |  |  |  | Closed | 12/17/2020 | 12/21/2020 | 12/21/2020 | 12/10/2020 | 12/10/2020
845 |  | 0 |  | GA005 | Request for Information | Wall Type 95 Unclouded Change in CCD_100 | Wall Type 95 changed in CCD_100, but the changes weren't clouded. Please verify that these changes were intentional. | If changes weren't intentional please update the sheet. | This wall type 95 change actually happened in CCD 106 which was submitted before CCD 100 and was still missing the revision cloud. Please include the change to the wall type as part of either CCD 100 or 106 whichever works. |  |  | Low | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 12/11/2020 |  |  |  |  | Closed | 12/20/2020 | 12/15/2020 | 12/11/2020 |  | 12/11/2020
846 |  | 0 |  |  | Request for Information | Courtyard Screen wall | The existing screen wall is an EIFS assembly with 2" of foam on one side and 1" on the other. Do we want to add the foam to the new screen wall to match existing? |  | Yes, match existing. ¦ |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 12/11/2020 |  |  |  |  | Closed | 12/18/2020 | 12/17/2020 | 12/15/2020 | 12/15/2020 | 12/11/2020
847 |  | 0 | 230000 | AE101A, M100B | Request for Information | Duct Chase clearances at West Stair Tower | Drawing AE101A indicates duct chase cavities located at grid H4 and H2 near HF. See attached drawing for clarification. These cavities are not shown/drawn the same size within the BIM model. Currently there exists a 6" difference in dimension. The south chase duct is clashing with the stud wall approximately 3.5". | Please adjust the wall duct chase cavity on the south to match the north chase and avoid the duct clash. | RFI 847 was reviewed with Jeff Adams at CRSA. Please adjust the highlighted walls shown in the attached pdf "20201216 SGT_RFI-847_VBFA" as needed to eliminate clashes between walls and ductwork and provide uniform sized chases at levels 0.5 and 1 in the west stair tower. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/14/2020 |  |  |  |  | Closed | 12/21/2020 | 12/17/2020 | 12/16/2020 | 12/15/2020 | 12/14/2020
848 |  | 0 |  |  | Request for Information | Thickened Edge - CCD 088r2 | After review of CCD 088R2, detail 8/LL501 has been added. This detail is not shown on any plans in CCD 088R2, but on CCD 88 it’s called out on plan LL102 (see attachment). The typical overall dimension for the paving band in that area is 1’-4”. It includes (2) 0’-4” & (1) 0’-8” nominal pavers and the new detail 8/LL501 is 1’-6” overall with (4) 0’-4” nominal pavers. It is not clear what the intent is on LL102. Does the band widen from 1’-4” to 1’-6” from the top of the plan down 12’-2”? Please clarify. |  | See attached response and updated sheet. ¦ |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 12/15/2020 |  |  |  |  | Closed | 12/22/2020 | 01/07/2021 | 12/22/2020 | 12/17/2020 | 12/15/2020
849 |  | 0 | 220000 | AE4009 | Request for Information | Urinal installation heights | Drawing AE4009, detail A5 shows a common wall for men's restroom 027. Both urinals shown are detailed to be installed at 1'5" to max to rim. | Common industry practice at walls with multiple urinals typically places heights at different levels to accommodate children or smaller persons of stature. See attached for reference. Please confirm all urinals throughout the project are to be located at 1'5" max to rim height and that no variances to this height are required/desired. | Please refer to architect regarding urinal mounting heights. ¦ Please keep all urinal mounting heights the same throughout at 17" max to top of rim. ¦ ¦ Please advise as to the desired mounting height for the Urinals'. |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 12/17/2020 |  |  |  |  | Closed | 01/07/2021 | 02/09/2021 | 02/05/2021 | 01/21/2021 | 12/17/2020
850 |  | 0 |  |  | Request for Information | CCD 088 Trench Drain Questions LL 101 and C.8 | From CCD 088-Plan sheet C.8 shows 3 trench drains in the north courtyard area. Note 99 on Sheet C.8 says new 4" wide slot drain connected to yard drain. On sheet LL 101, note S calls out a trench drain with an 8" x 18" Double Wave trench cover. Which size is correct for the trench drain, 4"or 8"? Also, the double wave trench cover from Urban Accessories has several different finishes which vary in price. Attached are the spec sheets for the double wave trench cover and the area drain covers. Which finish should this material have? Please provide further information so I can complete pricing for CCD 088. |  | Provide an 8" drain per sheet LL101. Finish for trench drain and square area drain covers to be 'Rust Conditioner'. ¦ See Greg's comment and use the 8" trench drain. ¦ The communication that I have had with the landscape architect team is that these are 8 inches to match the paving pattern. ¦ |  |  | High | Clint Foster | Sunroc Corporation | Civil Engineers |  | 12/18/2020 |  |  |  |  | Closed | 12/24/2020 | 02/03/2021 | 01/28/2021 | 01/13/2021 | 12/18/2020
851 |  | 0 |  |  | Request for Information | Plinth Material Throughout Temple | Looking through bid documents, we've noticed the plinth details for this project are all for wood plinths. Can you please clarify if stone plinths are needed in this project? If so, please provide specific locations, stone material, and a detail with the elevation and section profile of these plinths, so we can proceed to quote them with our stone fabricators. Thank you for your help. |  | all plinths to be wood. ¦ |  |  | High | Connor Cooper | GLOBAL STONE & TILE LLC | CRSA ARCHITECTURE |  | 12/21/2020 |  |  |  |  | Closed | 12/18/2020 | 01/14/2021 | 01/14/2021 | 12/22/2020 | 12/21/2020
852 |  | 0 |  |  | Request for Information | Doors and Jambs at rm. 218 and rm. 408 | Should door jamb 218A, 222A and celestial room side only door 222A have the inner small panel molding? Currently the jambs do not call for the inner molding, door 218A call for inner molding one side and door 222A have inner small molding both sides. Current historical doors have inner molding on doors and jambs. Doors 408A, 408B call for type 9 door inner molding both side. Door jamb 408A, 408B have no inner molding. Should door 408A, 408B, have inner molding one side and door jambs 408A, 408B and inner moldings on the jamb.? |  | What is stated is correct, inner molding on Doors and Jambs in the Celestial Room and Level 4 Assembly Room. Door 218 - Inner Molding only on East Side of Door (Celestial Room side) Door 218A - Inner Molding on Jamb Door 222A - Inner Molding on Jamb and South Side of Doors (Celestial Room side) Door 408 A & B - Inner Molding on Jamb and East Side of Door (Assembly Room Side) ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 12/21/2020 |  |  |  |  | Closed | 12/28/2020 | 01/07/2021 | 01/05/2021 | 12/22/2020 | 12/21/2020
853 |  | 0 | 230000 | ASI-042 M100A | Request for Information | ASI-042 missing scope items | ASI-042, drawing M100A appears to have added some fire smoke dampers at the exhaust ducts located along gridline HE. | Please clarify if these dampers have been added and provide cloud at the added scope as needed. | The FSD's in question will be added as part of CCD-138. ¦ ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 12/22/2020 |  |  |  |  | Closed | 01/28/2021 | 03/10/2021 | 03/05/2021 | 01/05/2021 | 12/22/2020
854 |  | 0 |  |  | Request for Information | CCD 088 Landscape Revision | Is there a detail showing concrete with a paver boarder as called out on LL101 |  | See attached for updated detail 5/LL501 for 8" paver band. ¦ |  |  | Medium | Melissa Carlisle | Innovative Concrete, LLC | Landscape Architects |  | 12/22/2020 |  |  |  |  | Closed | 12/29/2020 | 01/04/2021 | 01/04/2021 | 12/28/2020 | 12/22/2020
855 |  | 0 |  |  | Request for Information | Irrigation & Planting Clarifications on CCD88 for Parkstrip | Perry Bratt with Stratton and Bratt made a trip to St. George over the weekend to look at the possibilities of hand digging the irrigation trenches along 300 East in the park strip without damaging the tree roots. Neither he nor I can see any way to effectively do this work by any means other than a vacuum truck. Mechanical or hand digging may be too damaging to the roots. Our challenge presently is that we have not found anyone who will give us a quote for the use of a vacuum truck/trailer. We are still looking. Are we thinking right or should we plan on digging as carefully as is reasonable by hand, knowing that we will do some damage? Please advise on the method you recommend to dig the irrigation lines in this area. We also need to know if you want us to price out what we think will be needed since there is not an irrigation drawing for this work? We are also assuming that we can tie into the existing irrigation lines that go to this area and not have to run new sleeving/pipe to get to the area? We may need new sleeving so the lines are adequate for sod. Sheet LI 109 has a note to protect existing irrigation but the existing irrigation is drip and will not water the sod correctly as the sod is shown on Sheet LP101A. Please advise us as to what direction to take with the type of irrigation for this area, type of planting (sod as shown in CCD88 or plants as shown before), and if sod and spray heads are required then please advise on the method of trenching around the tree roots for this area as it is more densely populated with roots than other areas. |  | See attached response ¦ Please see our updated written response as well as our updated plan sheets in response to RFI-855. ¦ ¦ This would be better answered by our landscape architect team. |  |  | Medium | Jayson Christensen | Stratton & Bratt Landscaping | Landscape Architects |  | 01/22/2021 |  |  |  |  | Closed | 12/29/2020 | 02/03/2021 | 02/03/2021 | 01/05/2021 | 12/22/2020
856 |  | 0 |  |  | Request for Information | Lights at Stair 7 and 8 | The lights at stair 7 and 8 are not consistently placed could we be provided with placement and elevations? Also there is not a circuit or relay designation could we be provided with this? (see attachment) |  | The locations and elevations will need to be coordinated with Gloria Kummer. The circuit relays for Stair 7-5 are L3P3B-33, LCP-L3-5. For Stair 8-1 they are L3P3B-35, LCP-L3-6. ¦ The new fixtures shall be located in the same locations the previous fixtures were located. this was discussed and understood with Jason Fullmer. ¦ ¦ As requested by Breawna please review the the locations and provide feed back if necessary. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Interior Designer |  | 12/23/2020 |  |  |  |  | Closed | 12/30/2020 | 02/10/2021 | 02/09/2021 | 01/08/2021 | 12/23/2020
857 |  | 0 |  |  | Request for Information | Wood base at stairs | Detail C1, E1/AE511 calls for wood base detail at the stair skirts and landings. Stair #5 finish schedule does not clarify what the trim is at the skirt board , stair landings of floor, or floor level .05. Stair 1, 3, and 4 clarify what the base is at the lowest level but does not clarify the wood base on the stair itself . Please clarify the wood base at all stairs, floors at each level, landings, and skirt board exterior walls. | Wood base should be the same for entire stair floors, skirt board and landings. This allows all the trim to tie together | Wood Base, skirt boards and landings shall all match and be the same base type. The stairs are indicated once at the basement level Finish schedule (AE660). It is intended to continue to all levels. Stair 5 base is labeled 068-Stairwell on the finish schedule. This stair is also to be continuous through each level. The East Spiral Stairs 7 and 8 baseboards and skirting material are still waiting to be determined. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 12/28/2020 |  |  |  |  | Closed | 01/04/2021 | 01/07/2021 | 01/04/2021 | 12/28/2020 | 12/28/2020
858 |  | 0 |  |  | Request for Information | Layout for Vanity and Lighting Typ - Historic | Please provide layout dimensions for vanity sinks and vanity lighting typical at Historic Building restrooms. Priority is level 5 and 3 then the remaining. |  | Please see ASI 64R.9 for dimensions. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/04/2021 |  |  |  |  | Closed | 01/04/2021 | 02/17/2021 | 02/17/2021 | 01/04/2021 | 12/28/2020
859 |  | 0 |  |  | Request for Information | Lav and Soap Dispenser power | The Drawings are showing a J box under counters for powered Lav's and Soap Dispensers US. Mechanical supplied Lavs and Soap Dispensers require 1 GFI outlet under counter for each combination (1 Lav 1 Soap Dispenser) This is typ. at all powered Lav's and Soap Dispenser locations. (see attached example) |  | Provide duplex GFCI outlet at each lav/soap dispenser location. Verify power requirements of devices being provided will not overload current circuiting. If additional circuits are required notify engineer. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 12/30/2020 |  |  |  |  | Closed | 01/06/2021 | 01/07/2021 | 01/06/2021 | 12/31/2020 | 12/30/2020
860 |  | 0 |  |  | Request for Information | EF 1-07 power source | Can we relocate the power source for EF 1-07 from H2M0 to H1M0B which is closer they are both located in the annex basement? (please advise) |  | We see no issue with shifting the circuit to this panel. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 12/30/2020 |  |  |  |  | Closed | 01/06/2021 | 01/07/2021 | 01/06/2021 | 12/30/2020 | 12/30/2020
861 |  | 0 |  |  | Request for Information | Site Details-Curbs | The site curb details shown LL501 (detail 7) and C.13 (detail F) may need additional reinforcement. See attached drawings for purposed reinforcement. These curbs may crack and move during backfill and compaction if they are not placed on a footing with additional reinforcement. If accepted this change will come with an additional charge. Please advise |  | My response would be to leave it as it is detailed in the plans. We haven't had any issues with this in the past. Unless this situation is unique and the contractor can provide a convincing argument on why it might crack during backfill and compaction our recommendation would be to leave it as detailed. I talked with the landscape architects about their detail on sheet LL501 (Detail 7), and they said that their detail has been updated. Make sure you are referencing the current sheets. I have attached a screenshot of their updated detail. ¦ I am not sure what CCD has that change in it. Greg Boudrero could answer that for us. In regards to detail F on sheet C.13, my response would be to leave it as detailed. We haven't had any problems with that cracking or moving during construction. If the contractor is experiencing problems with cracking or movement then explain and we can further evaluate. I haven't experienced any problems with the way it is detailed out. ¦ ¦ Thank you for bringing the new detail to our attention. What CCD (or other) was revision delta 18 associated with? This is a solution, however it will have more of a cost impact than what we purposed. The extra form work and with a floating edge form it may not finish out as clean or straight as well. What about detail F on C.13? This may have the same issue as noted before. |  |  | Medium | Stormy Carlisle | Innovative Concrete LLC | Civil Engineers |  | 12/31/2020 |  |  |  |  | Closed | 01/07/2021 | 01/08/2021 | 01/06/2021 | 12/31/2020 | 12/31/2020
862 |  | 0 | 220000, 230000 | ASI#72, M101A, M102, M103, M104, M105 | Request for Information | West Stair Tower-Janitor Storage Ceiling | Following ASI# 72 review, it appears there exists conflicts with the current ceiling layout and required access for all plumbing and mechanical systems. Reflected ceiling drawings only show a single access door in these rooms. Due to the amount of access required to plumbing and mechanical systems, 2 or 3 doors will be required for service at each room along with relocating a few exhaust grilles. | Recommend changing the ceiling type in these janitor areas to lay in tile or eliminating the celings in their entirety to allow for sufficient access to the plumbing and mechanical systems. See attached for clarification. | i take no exception to providing lay-in ceilings in janitor closet locations. the elec sub may want to propose a new light fixture (recessed) to be installed at these locations if this change is made. we will review proposed fixture once recieved. ¦ Please reference Jason's email 01.04.2021 sent to Kyle. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 01/04/2021 |  |  |  |  | Closed | 01/11/2021 | 01/06/2021 | 01/05/2021 | 01/05/2021 | 01/04/2021
863 |  | 0 |  |  | Request for Information | East Tower floor boxes | There are floor boxes in rooms 317,319,517 and 519 that have historic plaster below preventing us from installing. Could we have an exception and install wall boxes in these locations? (see attachments) |  | These devices were already changed to wall mounted devices as part of RFI-787. ¦ Yes, These outlets can be wall mounted as indicated By Envision in RFI #787. See current conformed Drawings EP103 and EP105. ¦ Envision approved RFI 787 but CRSA did not |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/05/2021 |  |  |  |  | Closed | 01/15/2021 | 01/21/2021 | 01/19/2021 | 01/06/2021 | 01/05/2021
864 |  | 0 |  |  | Request for Information | TLC LED tape light at Monument Sign | TLC LED tape light requires a remote mounted Driver. Could we be provided with the location for these drivers at both monument signs? (see attachments) |  | Attached are (2) Drawings indicating Envision's proposed locations. We verified with the Landscape Architect that these locations will work with the planting plan; however, we recommend that they also be verified with CRSA. ¦ CRSA is good with the locations. Please see the attachments and comments below. ¦ ¦ Landscape Architect please confirm locations in response to this RFI. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 01/05/2021 |  |  |  |  | Closed | 01/12/2021 | 02/15/2021 | 02/11/2021 | 02/11/2021 | 01/05/2021
865 |  | 0 |  |  | Request for Information | West Stair Tower Embed Locations | There are 4 locations where the beams for the stair landings are into windows. I have attached a few screenshots to show the issue but if you are needing more let me know. For reference we have attached some elevations taken from the BIM model. Please advise |  | Please see attached sketches for proposed solution to the embed/window interference. ¦ |  |  | High | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 01/07/2021 |  |  |  |  | Closed | 01/09/2021 | 01/21/2021 | 01/18/2021 | 01/07/2021 | 01/07/2021
866 |  | 0 |  | ES200, ES501 detail #11, LP107A | Request for Information | Palm tree lighting detail | Related Scope: Landscape / Electrical Related Documents: ES200, ES501 detail #11, LP107A Description: Per ES501 detail #11 shows the lights for the palm trees. In that detail #11 is shows concrete encasing the light and connected to sidewalk or other concrete. Please confirm or adjust this detail as needed to provide the direction that is intended. |  | Detail 1/ES501 is intended to show both In-Grade and In-Concrete installations. For In-Grade installations use the Left Side of the detail, and for In-Concrete installations use the Right Side of the detail. Further, please read and follow the Manufacturer's Installation Instructions (provided with each fixture) when installing the fixtures. ¦ ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | David Tibbitts | ENVISION ENGINEERING | 01/08/2021 |  |  |  |  | Closed | 01/15/2021 | 01/21/2021 | 01/15/2021 | 01/15/2021 | 01/08/2021
867 |  | 0 |  | ES200, LL100, LP107A | Request for Information | East plaza bollard and pot location | Related Scope: Landscape / Electrical Related Documents: ES200, LL100, LP107A Related Spec: Description: Per LP107B the understory planting plan it shows the pot and it has understory plants where a light bollard is shown on ES200. Is it the intent for the light bollard to stay in the location shown on ES200 or does the pot and bollard need to be adjusted to be more symmetrical? |  | See attached response ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 01/08/2021 |  |  |  |  | Closed | 01/15/2021 | 01/21/2021 | 01/15/2021 | 01/08/2021 | 01/08/2021
868 |  | 0 |  |  | Request for Information | Stair 5 Underlayment | As we are laying in the stairs for the historic Temple, I wanted to clarify the final dimensions for the wood, etc. for planning purposes. The annex went with ¾” wood directly attached to the concrete pans. The details for the wood treads show 1.25” treads on what appears to be at least 1 layer of plywood – but I can’t seem to find any specifics. It is our understanding that the wood flooring is to be glued directly to the concrete. Please advise. For reference I have included some drawings showing the ¾” underlayment as well as an illustration provide by Glassey. | Revise drawings to show the plywood underlayment removed. | 1-1/4" Wood thickness is obsolete. 3/4" Wood flooring is to be applied directly to the concrete stairs. The wood flooring at the second level landing and in vestibule 222 that ties into the adjacent lobby 218 and instruction room 211 shall be installed over the new subfloor. This is to create an even transition from new wood to carpeted areas. |  |  | High | Brett Glassey | Glassey Steel Works | CRSA ARCHITECTURE |  | 01/08/2021 |  |  |  |  | Closed | 01/11/2021 | 01/21/2021 | 01/19/2021 |  | 01/08/2021
869 |  | 0 |  |  | Request for Information | Baptistry Font Tunnel Location | Please provide dimensions from gridlines to walls supporting the font tunnel as shown on the attached sheet S100A. |  | This was coordinated on-site and concrete side walls have already been poured. Please close out RFI. ¦ |  |  | High | Stormy Carlisle | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 01/11/2021 |  |  |  |  | Closed | 01/18/2021 | 02/08/2021 | 02/05/2021 | 01/12/2021 | 01/11/2021
870 |  | 0 |  | EL102B, AE4211 | Request for Information | Sealing Rm 3 Wall Sconce Dimensions | 1- Can we get dimensions for wall sconces in Sealing Rm 3 (Room 219). 2- Also, (2) wall sconces are shown on the west wall on EL102B, but they are not shown on the elevation B5 on page AE4211. Are they to be installed? If so we need those dimensions as well. | See attachments for further clarification. | The Decorative Fixtures, like Fixture Type: WS-4, are Specified by the Interior Designers, so Envision Engineering Does Not have the Dimensional Information requested. Further, Sheet AE4211 was created by the Architect, so Envision Engineering cannot address the Information Provided, or Not Provided on the Drawing. ¦ Dimensions have been provided on attached AE4211 Sconces Added to elevation and dimensions provided. ¦ ¦ Envision has responded in the comments. CRSA to review and Envision will coordinate as required. ¦ CRSA needs to look at this |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/12/2021 |  |  |  |  | Closed | 03/18/2021 | 03/18/2021 | 03/17/2021 | 01/21/2021 | 01/12/2021
871 |  | 0 |  | ES202 | Request for Information | Pole Light EP12B Heads | Pole lights EP12B have three (3) floodlights of types EFG & EFH - 2 of one and 1 of the other. Is it (2) EFG and (1) EFH? Or (1) EFG and (2) EFH? For reference we have attached sheet ES202 with the lights in question highlighted. |  | See Comment and Attachment for Clarification ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 01/12/2021 |  |  |  |  | Closed | 01/19/2021 | 01/13/2021 | 01/13/2021 | 01/13/2021 | 01/12/2021
872 |  | 0 |  |  | Request for Information | Loading Dock Concrete Replacement | See the attached pdf which discusses various sections of concrete that will/could be replaced around the loading dock. |  | Concrete has already been cut and removed. |  |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/12/2021 |  |  |  | 1.00 | Closed | 01/24/2021 | 03/03/2021 | 03/01/2021 |  | 01/12/2021
873 |  | 0 |  | EL101F | Request for Information | Lighting on wall next to dumpster enclosures | The existing lighting on the existing north wall of the cooling tower enclosure, and west of the dumpsters was installed for two light fixtures. The existing, recessed J-boxes and conduit are intact and usable. The new plan (EL101F) shows only one fixture. We would have to basically demo the wall and re-configure the conduit and boxes to work with one light fixture. Should we install two lights on the existing boxes, or open the wall up and re-work the conduit for only one light fixture? Please see the attached drawing for clarification. | Use existing boxes and wiring and install 2 light fixtures instead of 1 | We agree with and endorse Westland's recommendation. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 01/13/2021 |  |  |  |  | Closed | 01/20/2021 | 01/21/2021 | 01/15/2021 | 01/14/2021 | 01/13/2021
874 |  | 0 |  |  | Request for Information | Porthole Window GFRC Trim | We field verified the porthole window openings and found some discrepancies. Please review options A & B in the attachment and confirm the direction that we should follow. |  | CRSA prefers the modification of shape to work with the existing openings. this is the second option available in the attachment. |  |  | High | Dustin Williams | Unlimited Designs Inc. | CRSA ARCHITECTURE |  | 01/13/2021 |  |  |  |  | Closed | 01/24/2021 | 01/21/2021 | 01/21/2021 |  | 01/13/2021
875 |  | 0 | 220000 | P sheets | Request for Information | Filtrine Drinking Fountain DF-1 Access Panels | Following onsite review with Westland and TFM of drinking fountain DF-1 Filtrine Model access, TFM has requested optional access doors to be provided to install an isolation valve at fixture and maintenance access for P-traps behind marble enclosures typical at all DF-1 drinking fountains. | U.S. Mechanical has receieved preliminary pricing for the additional access doors being requested. See attached ROM and provide direction as to whether this issue should be pursued via COR/CCD. | Justin, Will you please provide a drawing of the access cover to insure it conforms to the project design. ¦ Per direction from the owner, access panels will be provided for access to p-traps and water isolation valves at the decorative drinking fountains where they can be feasibly located on the opposite side of the wall where the drinking fountains are located. For the few locations where this is not feasible, no access panel will be provided and the water isolation valve shall be located next to the the remote chiller above the ceiling. See the attached pdf "20210216 RFI 875_Drinking Fountain Access Panels" for notes about each drinking fountain location. ¦ Please see the attached document titled “Optional Access Panel Filtrene” for the look and location of the Optional Access Panel. For reference I have gone through and highlighted the access panels. |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 01/14/2021 |  |  |  |  | Closed | 02/18/2021 | 02/16/2021 | 02/16/2021 | 01/15/2021 | 01/14/2021
876 |  | 0 | 230000 | AE121, M101 | Request for Information | Security Room 123 HVAC grille type | Drawing AE121, Security Room 123 indicates a lay in tile ceiling. Drawing M101 indicates equipment FC-1-06, supply and return grilles with no call out for types or ductwork shown. | Please provide a grille selection and ductwork sizing for this space. See attached drawings for clarification. | This RFI will be answered with changes made in CCD-028 R.5. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 01/14/2021 |  |  |  |  | Closed | 01/21/2021 | 02/10/2021 | 02/09/2021 | 01/14/2021 | 01/14/2021
877 |  | 0 |  |  | Request for Information | Cable tray thru opening 002 | With opening 002 being replaced with a door we suggest rerouting cable tray on south side of wall and nippling thru to TR2 (See Attachment) |  | Confirmed. Detail 10/S201 will apply for this application. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Structural Engineers |  | 01/14/2021 |  |  |  |  | Closed | 01/21/2021 | 01/15/2021 | 01/15/2021 | 01/14/2021 | 01/14/2021
878 |  | 0 |  | S231 | Request for Information | Embed Location Fix | There are a couple embeds in the wrong location. This occurs at grid H1/HC as well as H1/HE Level 0.5. We are looking for a typical fix. Installing a similar size plate using 6 titan bolts or 6 epoxy anchors post installation to the jacket wall. | Use installation methods as shown in the attached drawings. | Use an embed plate similar to that shown in detail 13/S231. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 01/15/2021 |  |  |  |  | Closed | 01/21/2021 | 01/15/2021 | 01/15/2021 | 01/15/2021 | 01/15/2021
879 |  | 0 |  |  | Request for Information | Mechanical Enclosure Plaster | In the mechanical enclosure there is a wall as shown on the attached drawing and photo that currently does not show any finishes installed on the wall. Do you want us to leave it unfinished or do you want us to finish it to match the adjacent walls? |  | Finish to match adjacent walls. ¦ |  |  | Medium | Jay Webster | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/15/2021 |  |  |  |  | Closed | 01/22/2021 | 01/21/2021 | 01/19/2021 | 01/15/2021 | 01/15/2021
880 |  | 0 |  |  | Request for Information | Finish for Stone Base, Partitions, Drinking Fountains, Pews | The following stone materials and finishes were clarified in a meeting between Gloria (GHID), David Adams (Westland), Jose Duron (GST), Connor Cooper (GST) and Alejandro Vasquez (GST) on 01/13/2021. Please confirm the following direction given in the meeting: BS1 Thassos White Marble stone base will have a polished finish. Countertop for Room 148a Closet in Ariston White Marble will have a polished finish. Thassos White Marble and LVR Sandstone thresholds will have a polished finish. Toilet Partitions will be Ariston White Marble and will have a polished finish. Pew Base will be Ariston White Marble and will have a polished finish. WST1 Ariston White Marble drinking fountains will have a polished finish. Thank you, Global Stone and Tile |  | This information is correct. However for the LVR we discussed getting a sample in honed and polished with enhanced sealers added. This is because they had already started production on the floor in honed. They were also going to layout the LVR floor tile with enhanced sealers and take a photo. This is because we never got the chance to review the slabs in digital form to mark the areas we rejected so we want to see what it looks like for color purposes, as well as with the sealer. If a trip is required we can look at it in person, but let's start with photos and the physical samples. ¦ |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 01/15/2021 |  |  |  |  | Closed | 01/18/2021 | 01/15/2021 | 01/15/2021 | 01/15/2021 | 01/15/2021
881 |  | 0 |  |  | Request for Information | Interior Font Tile Finishes | In a meeting between Gloria (GHID), David Adams (Westland), Jose Duron (GST), Connor Cooper (GST) and Alejandro Vasquez (GST) on 01/13/2021. Please confirm the Interior Font Finishes were discussed and approved as followed: WT2 Font Wall Tile pattern designed in CCD 040R3 will not work with the radiused walls (because of 2x4 tile and 2x2 triangles). Instead, we proposed the pattern to be all made up of 1x1 tile in the different colors. Attached is how the pattern will look with all 1x1 tile (note that Daltile has already confirmed they can produce this pattern). Gloria approved this revised pattern. Font stair nosing piece in Finish Schedule is called out as A4200 Radius Bullnose. Daltile has called out this piece to actually be S-812 Universal Trim 1x1. Even though Daltile has confirmed this piece is available in D169 Waterfall (blue) color, Gloria's preference is that the nosing piece will be D335 Almond. The following 4 rows of 1x1 tile after the nosing piece will be D169 Waterfall (blue) as shown in the attachment and as approved by Gloria Please confirm. Thank you, Global Stone and Tile |  | This layout to adjust the tile size to fit the radius of font is approved. Thanks for figuring it out! ¦ |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 01/15/2021 |  |  |  |  | Closed | 01/22/2021 | 01/26/2021 | 01/26/2021 | 01/15/2021 | 01/15/2021
882 |  | 0 |  |  | Request for Information | Stone Toilet Partitions - Design and Structural Support | Marble Thickness: Contract drawings show the toilet partition stone to be 3/4" thick. We believe this is too fragile for the application. We priced and recommend using 1-1/4" (3cm) stone. Please confirm this is acceptable. Structural Support: The hardware design for WST1 Ariston White Marble toilet partitions shown in contract drawings does not provide enough detail for us to feel confident that they can support marble slabs (see attachment). Please provide additional details on how these are intended to be supported. Details coming directly from the hardware supplier will be preferred. Hardware Supplier: Please provide the approved manufacturer/supplier for toilet partition hardware that will be used in this Project (We only provide the stone panels - per project specifications. Wood doors and partition hardware is provided by others). |  | Stone restroom partitions have been omitted from the project per CCD -128. |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | CRSA ARCHITECTURE |  | 01/15/2021 |  |  |  |  | Closed | 01/22/2021 | 02/15/2021 | 02/11/2021 | 01/15/2021 | 01/15/2021
883 |  | 0 |  | LL108 | Request for Information | Fiber box Sidewalk Conflict East of Visitor Center | The existing fiber connection and electrical boxes for the visitor center are located where sidewalk is shown (see attached pdf). We will need to reroute the sidewalk in some way to avoid them. We propose a possible radius something like what is in green on this corner. Please advise. |  | See attached for updated plans showing a shift to the location of the walkway. ¦ Please refer to these additional planting plan sheet that cover the shift in the sidewalk |  |  | High | Russ Hanson | Westland Construction, Inc. | Landscape Architects |  | 03/19/2021 |  |  |  |  | Closed | 01/22/2021 | 03/22/2021 | 03/19/2021 |  | 01/18/2021
884 |  | 0 |  |  | Request for Information | FT1 and FT2 - Floor Pattern Layouts and Color Schemes | In a meeting on 01/13/2021 between Gloria (GHID), David (Westland), Jose (GST), Alejandro (GST) and Connor (GST), we discussed our proposed floor pattern layouts for FT1 and FT2 Victorian Topcer designs. The following items were part of our discussion: GST laid out floors using full border pieces. Per Gloria's instructions, we need to modify the layouts to show an average of 5-6 filler pieces on the edges of the rooms, while still mantaining full triangles in the border tile (even if we have to cut the border tile and add a grout joint). We have attached updated floor layouts for all bathrooms with FT1 and FT2 floors. Please confirm these updated layouts are acceptable. Gloria mentioned there will be a change in color schemes for the FT1 and FT2 floors, from what is currently shown in CCD 040R3. We urgently need a directive of what the new colors will be for these Topcer floors so we can order this material (12 week lead time). Thank you, Global Stone and Tile |  | This was answered in a CCD 040r4 ¦ |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 01/18/2021 |  |  |  |  | Closed | 01/21/2021 | 03/03/2021 | 02/23/2021 | 01/21/2021 | 01/18/2021
885 |  | 0 |  |  | Request for Information | TW2/TW3 - Color Changes | In a meeting on 01/13/2021 between Gloria (GHID), David (Westland), Jose (GST), Alejandro (GST) and Connor (GST), Gloria mentioned the TW2/TW3 wall trim tile (attached pictures) will change to only include the green scheme tile (TW3) while removing the blue scheme tile entirely (TW2). This is different than what is currently shown in CCD 040R3. We need a directive urgently to confirm this change so we can continue the procurement process for these materials (12 week lead time). Thank you, Global Stone and Tile |  | photos are notated to clarify the green tile is to be used. |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 01/18/2021 |  |  |  |  | Closed | 01/21/2021 | 01/26/2021 | 01/26/2021 | 01/21/2021 | 01/18/2021
886 |  | 0 |  |  | Request for Information | Confirm outlet dimensions 3rd & 5th floor East vestibules | As per RFI's 787 and 863 we are putting the outlets and data ports into the walls in the 3rd and 5th floor East vestibules (instead of floor boxes). Please confirm that the dimensions are correct as shown in the attachments. Boxes will be mounted at the standard height of 18" AFF to center. |  | The outlets for these rooms have been changed to be wall mounted. This includes rooms 318 and 518. Room 518 does have one floor box in front of the window per plan. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/28/2021 |  |  |  |  | Closed | 01/28/2021 | 02/23/2021 | 02/18/2021 |  | 01/21/2021
887 |  | 0 |  |  | Request for Information | Gate Control j box | Gate control j box is shown on unsecure side of fence could we be provided with a location? (see attachment) | Locate inside landscapers shed | Envision is fine with locating the junction box for gate controls in the landscapers shed. As long as this will meet all MFG requirements for distances, etc. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 01/21/2021 |  |  |  |  | Closed | 01/28/2021 | 01/22/2021 | 01/21/2021 | 01/21/2021 | 01/21/2021
888 |  | 0 |  |  | Request for Information | Clear story EIFS | The center tower on the north end of the annex is off center. Also the wing walls on the annex clear story are not flush with the precast panels. Jay has suggested that we fix both situations by adding additional foam with the EIFS system. Jay and I have already had a meeting with the architect and all agree this is the best solution. Will you please confirm these changes? Thank you. |  | Adding an additional few inches of foam to the EIFS system to center the tower is acceptable. ¦ |  |  | High | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 01/21/2021 |  |  |  |  | Closed | 01/28/2021 | 02/09/2021 | 02/05/2021 | 01/21/2021 | 01/21/2021
889 |  | 0 |  |  | Request for Information | Scaffolding on Brides Hallway Weight Limit | Please see the attached scaffolding plan. Please verify that the weights shown are acceptable or provide further information on what weight would be accepted in this location. |  | Based on a discussion with Westland and the scaffold guys this morning, it was determined that the load on each scaffold leg would be no more than 2,000lbs. Provided that the scaffold loading is limited to 2,00olbs the slab on metal deck has the capacity to support those loads. It is expected that all other loads on the floor will be limited to human traffic and no items will be stock piled or stored on the slab in this area. ¦ * ¦ Zach, thanks. |  |  | High | Jay Webster | Westland Construction, Inc. | Structural Engineers |  | 01/22/2021 |  |  |  |  | Closed | 01/29/2021 | 01/27/2021 | 01/27/2021 |  | 01/22/2021
890 |  | 0 |  |  | Request for Information | FT1/FT2/FT5/FT6 Color Scheme Changes | On 01/22/2020 we received a tile sample submittal review from Gloria that changed some tile colors within the FT1, FT2, FT5 and FT6 floor patterns. Please confirm the following: FT1/FT2 (Topcer floors): Generic color names are used in the markups for the Topcer pattern changes. We don't want to move forward with our assumptions without confirmation of what the "tan", "red" and " green" actually are. Please confirm "tan" is "#03 Yellow", "red" is "#20 Brick Red" and "green" is "#28 Light Green" (see attached Topcer color chart). FT5/FT6 (Daltile floors): For Daltile Keysonte Mosaic FT5 and FT6, please confirm "white" is "AO #078 Capuccino" and "tan" is "D335 Almond". Thank you, Global Stone and Tile |  | Dal tile clarification: Tan is the A078 Cappuccino. White is D335 Almond Topcer colors noted correctly. See attached. |  |  | High | Jose Duron | GLOBAL STONE & TILE LLC | Interior Designer |  | 01/22/2021 |  |  |  |  | Closed | 01/25/2021 | 01/26/2021 | 01/26/2021 | 01/25/2021 | 01/22/2021
891 |  | 0 |  |  | Request for Information | Scaffold at Historic Level 2 - RM 218 | Please see the attached scaffolding plan. Please advise if the weights indicated are acceptable. |  | Please support each scaffold column on cribbing planks that span across a minimum of (4) floor joist. In order to use the scaffold in this manner, no other material or loads etc. should be placed on the floor in the scaffold area. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Westland PE’s |  | 01/22/2021 |  |  |  |  | Closed | 01/29/2021 | 01/25/2021 | 01/25/2021 |  | 01/22/2021
892 |  | 0 |  |  | Request for Information | 4th Flr Vest. 409 WAP location | Could we get a dimensioned detail of where the WAP goes on the ceiling of vestibule 409 on the 4th floor? See attachment. |  | Please refer to ASI #90 reflecting dimensions. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/25/2021 |  |  |  |  | Closed | 02/01/2021 | 02/11/2021 | 02/11/2021 | 01/25/2021 | 01/25/2021
893 |  | 0 |  |  | Request for Information | Annex L0 Mech Room Penetration | Please see the attachment that shows penetrations through an existing concrete wall. Please provide a detail similar to 11/S201, however, for how to tackle this < 3'D' condition on this existing concrete wall. |  | This item was addressed while Brent White was on site. It was determined that the proposed layout shown to Brent was acceptable and the cores could be made. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 01/25/2021 |  |  |  |  | Closed | 02/01/2021 | 02/09/2021 | 02/09/2021 |  | 01/25/2021
894 |  | 0 |  |  | Request for Information | Recessed Can Vs Joist Conflict | See the attached that shows 3 different RCP plans and where the recess can lights clash with the joist above. Please provide further direction. |  | Contractor needs to include proposed locations to avoid joists and resubmit RFI for approval and adjustments from Envision Electric and CRSA. |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/25/2021 |  |  |  |  | Closed | 02/06/2021 | 02/18/2021 | 02/18/2021 |  | 01/25/2021
895 |  | 0 |  |  | Request for Information | Columns at Gridlines HC/H3 | Please advise if the attached fix will be acceptable for joist attachment on the column at the intersection of gridlines HC/H3. This was reviewed on site with the Brent, Josh and Will where it was mentioned that the attached detail was close but there were some adjustments that may need to be made to it. |  | Please see attached sketch for required connection. It is similar to the suggested detail with a few more added stiffener plates. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 01/26/2021 |  |  |  |  | Closed | 01/28/2021 | 01/28/2021 | 01/28/2021 |  | 01/26/2021
896 |  | 0 |  | M411 | Request for Information | Cooling Tower Piping | Please see the attached notations on cooling tower piping location change as discussed with VBFA and TFM. Please advise if we are to proceed with this change and provide any specific requirements as needed. |  | Provide 2" connections for the cooling tower filter piping in the locations as indicated in the attached pdf "M411 - MECHANICAL ENLARGED PLANS & SECTIONS - CT Piping RFI". The cooling tower filter pipe routing will be updated and reissued to show connecting to the cooling towers in the new locations. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Mechanical Engineers |  | 01/26/2021 |  |  |  |  | Closed | 02/02/2021 | 02/16/2021 | 02/16/2021 | 01/26/2021 | 01/26/2021
897 |  | 0 |  |  | Request for Information | East Basement Doorways | As we are preparing to make the saw cuts into the east doorways (Chapel to Confirmation rooms, Confirmation rooms to Stairs) we had a few questions. The first issue is at the stairway wall. This is a radius wall that will get a C channel attached to support the stone while the cut is made. Can we shim behind the C channel with lumber to maintain the squeezing effect? The other issue is the length of the C channel. We currently have holes drilled 6 inches past the sides of the doors, do we need to extend these holes further? |  | The idea of using wood shims sounds like a good approach and we don’t take issue with that. For the C channel length, the channel needs to extend past the opening on each side a minimum of 24”. That 24” extension needs to have bolts in it as well so you will need to drill a few more holes. |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 01/26/2021 |  |  |  |  | Closed | 01/29/2021 | 01/27/2021 | 01/27/2021 |  | 01/26/2021
899 |  | 0 |  |  | Request for Information | East Side Level 5 Ceiling | Please confirm that the areas in Yellow are to me installed as gypsum suspended ceiling with plaster this will eliminate the concerns regarding the attachment method to the ruble stones. This will aid with the installation for the crown and other finishes. |  | Please refer to CCD 124 - 5th floor ceiling changes that was sent out for approval on 01-29-21. |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 01/26/2021 |  |  |  |  | Closed | 01/29/2021 | 02/02/2021 | 01/29/2021 |  | 01/26/2021
900 |  | 0 |  |  | Request for Information | Duct Smoke Detectors at AHU's | There are several AHU supply and return ducts that immediately split when leaving the AHU. Can we locate the detectors inside the AHU,s with sample tubes in the supply discharge before the steam is introduced into the air flow (this would also reduce the chance or false alarms caused by the steam)? And can we locate the detector at the return inside the AHU with the sample tubes located across the return air opening. otherwise a duct detector would be required for each split in the duct? |  | We have no problem with installing the smoke detectors in the air handler as long as code allows it. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Mechanical Engineers |  | 01/27/2021 |  |  |  |  | Closed | 02/26/2021 | 03/10/2021 | 03/05/2021 | 01/27/2021 | 01/27/2021
901 |  | 0 |  |  | Request for Information | Electrical Plan Reversions | See the attached PDF showing an overlay of CCD_108 and CCD_95R1 on page EP101. CCD_108 (in red) on sheet EP101 is dated after and therefore supersedes CCD_95R1 (in green) on the page. I don't believe this is correct. I don't believe the intent was to move the ADA operators in CCD_95R1 and then move them back to their original location in CCD_108. This issue makes me question various electrical plans that have changes that appear to be reverted later on. Please reissue a verified current version of at least EP101, EP101A, EP201, EP801, EP802, & EP803. I believe this is some disparity between CCD_95R1, CCD_104R1, and CCD_108; you might consider reissuing a current version of all electrical pages or the ones associated with those changes. |  | Updated drawings posted and verified with CCD-095R1 and CCD-108. I don't see where any changes for CCD-104R1 were made in the electrical model. See comment about changes on EP802 for upcoming CCD. |  |  | High | Camron Walker | Westland Construction, Inc. | Electrical Engineers |  | 01/27/2021 |  |  |  |  | Closed | 01/30/2021 | 02/02/2021 | 01/28/2021 |  | 01/27/2021
902 |  | 0 |  |  | Request for Information | Interior Bench Finishes | Please clarify the items that are to be stained vs what items are to be painted. Additionally, please confirm that the paint for the white components of the bench are intended to match the finish trim. For ease of access I have attached the color as called out in a paint submittal. |  |  |  |  | Medium | David Adams | Westland Construction, Inc. | Interior Designer |  | 01/27/2021 |  |  |  |  | Closed | 02/03/2021 | 02/03/2021 | 02/03/2021 | 01/28/2021 | 01/27/2021
903 |  | 0 |  |  | Request for Information | outlets rm 132a/interior elevations rm168&169 | Structural framing is preventing us from using provided layout at room 132a could we be provided with interior elevations for rooms 168&169 (see attachments) |  | We are Ok with both devices moving to the south wall in 132A. We have asked architectural to provide elevations of those rooms. Electrical device locations have been verified in the model. ¦ Moving the electrical devices to the south wall of 132a is acceptable. Please see attached ASI #89 for the dimension clarifications of rooms 168 and 169. ¦ Please review the attachment for further information. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 01/28/2021 |  |  |  |  | Closed | 02/04/2021 | 02/03/2021 | 02/03/2021 | 02/02/2021 | 01/28/2021
904 |  | 0 |  |  | Request for Information | Vehicular Concrete | Please clarify the Vehicular Concrete detail. Bid set and conformed set, LL501 detail 3 & 4, showed a 6" concrete thickness (see attached). It appears there was a revision delta 8/CCD 8 where this detail was revised (see current attached). Innovative Concrete never received this CCD. Please confirm LL501 detail 3, 4, 7 & 8 are correct. Now showing vehicular concrete at an 8" thickness. |  | The LL sheets are the landscape architect sheets. ¦ Please refer to CCD 119. ¦ ¦ RFI to the landscape architects, please respond. Thanks |  |  | Medium | Stormy Carlisle | Innovative Concrete LLC | Civil Engineers |  | 01/28/2021 |  |  |  |  | Closed | 02/04/2021 | 02/09/2021 | 02/08/2021 | 01/29/2021 | 01/28/2021
905 |  | 0 |  |  | Request for Information | Stair 5 Steel Placement | In Stair 5 there are some locations where the steel is overlapping the stone buttresses. We have RFI’ed and received a response saying the center column is to be cut flush with the stone wall but the two buttresses on the East and West side have not been addressed. This question was reviewed with Zach and David A when he was on site 01-28-2021. For reference and illustration please see the attached email. |  | See attached for response. ¦ |  |  | High | Brett Glassey | Glassey Steel Works | Structural Engineers |  | 01/29/2021 |  |  |  |  | Closed | 02/01/2021 | 02/02/2021 | 02/01/2021 | 01/29/2021 | 01/29/2021
906 |  | 0 |  |  | Request for Information | Entry Door Leaves Operator | After walking the job with the electrician, our installer and Jason Fullmer. A Question came up regarding openings 100A, 101A, 101B and 102B currently they only have one leaf open with the auto opener. Please advise do both doors leaves need to open in these openings? |  | Only one leaf is to be auto operated at these doors as specified. ¦ |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/02/2021 |  |  |  |  | Closed | 02/06/2021 | 02/22/2021 | 02/18/2021 | 02/02/2021 | 02/02/2021
907 |  | 0 |  |  | Request for Information | Temple Custom HDW Submittal - Rocky Mountain | One thing to note, we’re not able to relocate the lever to 3-1/2” above the bottom of the plate as the cylinder will encounter the bead detail. I’ve located the lever 3-1/4” from the bottom instead. If you need the 3-1/2” spacing, we can increase the overall height of the escutcheon to make room for the cylinder. Let me know which route you’d like to take. Alternatively would it be acceptable to shift the Lever and the and the Cylinder so the Cylinder is adjacent to the top of the beaded area with an equal distance from the sides and the top? Then we raise the Lever to keep the 3-27/32” as shown in the attached drawings? |  |  |  |  | Medium | Russ Farley | Architectural Building Sup | CRSA ARCHITECTURE |  | 02/02/2021 |  |  |  |  | Closed | 02/09/2021 | 02/03/2021 |  | 02/03/2021 | 02/02/2021
908 |  | 0 |  |  | Request for Information | Pre-cast at fountains | See attached |  |  |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Westland PE’s |  | 02/03/2021 |  |  |  |  | Closed | 02/10/2021 |  |  |  | 02/03/2021 | Final
909 |  | 0 |  |  | Request for Information | Aluminum Threshold Profiles | Thresholds shown on details A1 and D3/AE634, D6/AE635 and E1 and E2/AE636 call for Stock Metal Thresholds. Is there a part #? I can’t find one that meets the given profiles. |  | No specific profile was used when detailing CRSA thresholds. It is acceptable to use standard profiles provided by the sub that meet the general requirements of flooring change as seen in our detail. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/03/2021 |  |  |  |  | Closed | 02/10/2021 | 03/22/2021 | 03/19/2021 | 02/03/2021 | 02/03/2021
910 |  | 0 | 262726 |  | Request for Information | Screwless Plates for Wiring Devices | See attached wiring device review from GHID. They are requesting screwless plates on wiring devices which are more expensive than the standard plates we submitted on. The specifications don't call for the screwless type plates and with the quantity of devices on this project the added cost will be approximately $1,700. Please confirm this is the case and that we can submit additional costs. |  | Approved by Eric and Team to move forward with screwless wall plates. ¦ |  |  | Medium | David Barney | Wilkinson Electric Inc | Interior Designer |  | 02/04/2021 |  |  |  |  | Closed | 02/11/2021 | 03/03/2021 | 03/03/2021 | 02/04/2021 | 02/04/2021
911 |  | 0 |  |  | Request for Information | Bride's exit outside ADA button | The bride's exit is now showing an ADA button on the outside of the door. Conversations were held with the Temple Head of Security and TFM. It was determined that this button could not be used since this is a locked door and not manned. Opening it from the outside by pushing a button cannot be allowed. They couldn't come up with a scenario it would be usable, but multiple scenarios where it will cause problems. See attachment. | Can we eliminate the ADA button outside of the Bride's Exit? The door would be operated by the inside push button. | Verify latest electrical plans are being referenced. This exterior operator should have been removed from plans as part of CCD-095R1 on 11-06-2020. ¦ See response from Envision Engineering. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/04/2021 |  |  |  |  | Closed | 02/11/2021 | 02/08/2021 | 02/08/2021 | 02/04/2021 | 02/04/2021
912 |  | 0 |  |  | Request for Information | MC cable for lighting | Could we be given an exception to use MC cable for all of our recessed can lighting. The J boxes provided on the can housings will not accept (2) .75" conduits. This would also provide flexibility both up and down and side to side for any future moving of the cans. |  | MC cabling may be allowed for recessed can lighting as requested given that it is limited to the areas immediately around the fixtures and not used for home run purposes. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/04/2021 |  |  |  |  | Closed | 02/11/2021 | 02/09/2021 | 02/09/2021 | 02/04/2021 | 02/04/2021
913 |  | 0 |  |  | Request for Information | Decorative Countertop Bracket | I have reviewed the information for ASI 079 that was sent to us and request a conformation for the design along with further question on how we are to proceed: Design: The idea is to use the “Yesterhome Hardware and Homeware 10” x 12” cast iron bracket" as the basis of design and resize it with similar detailing to be 16” x 20”. No problem, HACI has the design staff and the pattern making staff to do that work. Desired Material: Stainless Steel. HACI does not have the capacity to make stainless steel castings. HACI can offer the following (They are listed in order of HACI’s preference, and in order from least expensive option to most expensive option): 1. Make the brackets from cast bronze - same material that we are already using on other parts of the project. 2. Make the brackets from cast white bronze - this is a cast bronze alloy with a higher nickel content which gives the material its name as it appears more silver in color than standard bronze and in many cases is considered a good substitute for stainless steel. 3. Make the brackets from machined and fabricated stainless steel. The body of the brackets would be machined from thick stainless-steel plate material, and the wider flanges that run along to the top and along the wall side would be made from thinner plate material. Finish: No information relative to the desired finish was found in the ASI 079 materials. |  |  | CRSA ARCHITECTURE |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/04/2021 |  |  |  |  | Forwarded | 02/11/2021 |  |  | 02/04/2021 | 02/04/2021
914 |  | 0 |  |  | Request for Information | PEW BENCHS #110 #62 #67 Fabrics and New Layout | 1) Please verify Chapel#110 Pew Fabric Mill – style – Color. Please ship only 6 yards WITH Pew Backing for testing to address above. (if it’s a different style than Chapel#62 and #67). 2) Please verify Fabric for Chapel#62 and #67 Grey Watkins – Stark YS002-1283. Fabric is medium grade 25000 to 30000 DR. Normal pews have High Grade 50,000 DR or higher Note High content of Cotton concern. Fabric will need to be tested – New Holland will provide test results. Pass/Fail. Standard Fabric Waiver will be submitted after testing for All COM fabrics. Fabric has 13.5W by 13.5H pattern must be Railroaded style down the roll. – Please verify railroad. Please ship only 6 yards of fabric WITH Pew Backing to address above. 3) Please see attached Drawing St George Temple Chapel Pews Revised 29JAN21 COMPLETED NOTE Drawing changed Per Instructions by GHID – ALL Pew Lengths Changed per GHID color coded instructions using Inside measurements provided to NHCF. Drawing reflects all changes requested and we have provided OUTSIDE and INSIDE pew lengths. 4) CHANGE TO PEW BODY DETAIL –per Scott, Eric, Ryan, and David. Note change to fabric backs per Instructions – fabric END TO END full length on backs. Backs will have white paint above the fabric then stained caprail – TWO TONE. |  | Please proceed with continuous upholstered back. GHID to provide % of fabric content custom sample as soon as available. New Holland to confirm if they would like both an acrylic back and knit back, or just an acrylic back. Once custom fabric is made option for New Holland to make final decision on backing once they receive the fabric. Otherwise we can ship directly to the treatment facility to backing and then ship to New Holland. ¦ |  |  | Medium | Danny Groves | New Holland Church Furniture | Interior Designer |  | 02/04/2021 |  |  |  |  | Closed | 02/11/2021 | 02/05/2021 | 02/04/2021 | 02/04/2021 | 02/04/2021
915 |  | 0 | 233300 | M101 | Request for Information | CCD 28R3 shear wall openings | Drawing M101, waiting room 109 at the AD and AE shear walls there are three(3) 20"x10" HVAC openings at each wall. Per CCD#28R3 direction these opening now require fire dampers. Spec section 233300, subsection 2.8, paragraph F calls out for a curtain type fire damper with blades out of the air stream. This will require the existing current openings to be increased to 20" x 12.5". The shear walls have been poured with the original 20" x 10" opening sizes. | Please advise if opening sizes are to be increased or other dampers not requiring opening size adjustment can be utilized. See attached drawings for clarification. | It is acceptable to increase the size of the penetrations as described. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Structural Engineers |  | 02/05/2021 |  |  |  |  | Closed | 02/12/2021 | 02/09/2021 | 02/09/2021 | 02/08/2021 | 02/05/2021
916 |  | 0 | 233519 | Mechanical Drawings | Request for Information | Dryer Exhaust Fire Wrap | Following a review of mechanical drawings indicating dryer exhaust install and routing, we have been unable to locate where it might call or show for the exhaust to be fire wrapped. Spec section 233519, part 2, section 2.2, paragraph F calls for 2 hour fire barrier wrap where shown. Please advise if the dryer exhaust duct is to be fire wrapped per spec and if so where it is required. |  | Code requires that laundry exhaust ducts maintain a clearance to combustibles of at least 6". Wherever the clearance to combustibles is going to be less than 6", fire wrap insulation needs to be installed. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/05/2021 |  |  |  |  | Closed | 02/12/2021 | 02/10/2021 | 02/10/2021 | 02/09/2021 | 02/05/2021
917 |  | 0 |  |  | Request for Information | Camera 20 | Per instruction on site by Ray Anderson with Brian Chandler and Trask present. We were instructed to install camera 20 at its original location on the east wall of the mech pit (see picture) we are asking for confirmation if this is correct. (see attachments) |  | Envision was not present and will defer to the Church security team for where to install this camera. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/08/2021 |  |  |  |  | Closed | 02/15/2021 | 02/10/2021 | 02/09/2021 | 02/09/2021 | 02/08/2021
918 |  | 0 |  |  | Request for Information | Fire Alarm and Generator Annunciators in TFM office | Please provide the elevation of the Fire Alarm Annunciator (22"W x28"T) and the Generator Annunciator (10" X 10") they are both located on the north wall of the TFM office (RM.045) |  | see power detail sheet EP501 for typical devices mounting height requirements. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/08/2021 |  |  |  |  | Closed | 02/16/2021 | 02/10/2021 | 02/09/2021 | 02/09/2021 | 02/08/2021
919 |  | 0 |  |  | Request for Information | West Wall Embeds at Doorways | Per a phone conversation between Josh Nay and Zach Hanson please advise on the installation of detail 14/S221. The embeds call for 2’ o.c. but the doors are roughly 3’ wide. How do we want to carry the ledger through these locations? |  | The embeds on each side of the door way need to be placed 14" from edge of door opening to centerline of nearest anchor bolt. An additional embed needs to be placed at the center of the door opening, but must be placed lower such that the top of the embed plate is flush with the bottom of the floor slab. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 02/08/2021 |  |  |  |  | Closed | 02/15/2021 | 02/23/2021 | 02/22/2021 | 02/08/2021 | 02/08/2021
920 |  | 0 |  |  | Request for Information | 3rd Floor Plaster Thickness | The stone wall on the 3rd floor has a bulge around the window in the center of the wall. By spec we are only to put 1/8 plaster on this wall will you confirm. Creg Norton talked with Scott and Kyle with CRSA regarding this and the 1/8” plaster cover was agreed on. Please confirm |  | Confirmed. The Historic stone walls on this floor have some minor variations, not being square or totally plumb. CRSA's understanding is that these are fairly minor and expected. Please continue with the original design intent with the patch/repair and plastering over the existing stone. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/08/2021 |  |  |  |  | Closed | 02/15/2021 | 02/23/2021 | 02/19/2021 | 02/08/2021 | 02/08/2021
922 |  | 0 |  |  | Request for Information | Trench Drain Size at Baptistry Door | Please advise if the trench drains are to be 8” as given for the main entrance in RFI 850, 6” indicated in Civil or 3 1/2” indicated in landscaping drawings. The pavers in this area are 8”. | Please confirm the trench drain is to be 8”. | See attached updated detail clarifying the detail. ¦ I believe Greg's comment on the 10th, should resolve this. If not, let us know. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Civil Engineers |  | 02/09/2021 |  |  |  |  | Closed | 02/15/2021 | 03/22/2021 | 03/22/2021 | 02/09/2021 | 02/09/2021
923 |  | 0 |  | EY100 | Request for Information | Fire Alarm Devices at Door 020A | Two Fire Alarm devices are shown at the corridor side of door 020A. See attached. Please advise if both are to remain. |  | Only one is required after the hall changes. Keep the device on the right side of the door. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Electrical Engineers |  | 02/09/2021 |  |  |  |  | Closed | 02/16/2021 | 02/10/2021 | 02/10/2021 | 02/09/2021 | 02/09/2021
924 |  | 0 |  |  | Request for Information | Stone Penetrations at Level 5 | Please confirm that per email Dated 02/09/2021 between Jason Fullmer and Zach Hanson that we are okay to proceed removing the stone at level 5 vestibule openings above the door portals. There will not be any steel plate inserts at these 2 openings. |  | Confirmed ¦ |  |  | High | David Adams | Westland Construction, Inc. | Structural Engineers |  | 02/09/2021 |  |  |  |  | Closed | 02/12/2021 | 02/12/2021 | 02/11/2021 | 02/09/2021 | 02/09/2021
925 |  | 0 |  |  | Request for Information | Pre-Cast Concrete Paving Submittal | In the latest return submittal #3 for site work, the fountain stone cap radius was marked up to be 4’9”. In submittal #2 the concrete radius was marked up to be 4’ 8. The cap hangs over the concrete 5-1/2” to cover the top of the precast, this would make the cap radius 5’ 1-1/2”. Please clarify. |  | ¦ See attached for a response |  |  | High | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 02/10/2021 |  |  |  |  | Closed | 02/13/2021 | 02/18/2021 | 02/17/2021 | 02/10/2021 | 02/10/2021
926 |  | 0 |  |  | Request for Information | East plaza pull box | (see attachment) there is a pull box that appears to be placed in concrete is this necessary? if so can it be relocated to landscaping. |  | This box can be relocated to the landscaping area. coordinate with planting plans on the best location. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/10/2021 |  |  |  |  | Closed | 02/17/2021 | 03/03/2021 | 03/02/2021 | 02/10/2021 | 02/10/2021
927 |  | 0 |  |  | Request for Information | East Plaza Fence | The height of the metal fence and the finish grade elevations conflict making the metal fence higher than the concrete portion of the fence. Please provide direction. |  | The metal fence will become concrete panels and that will step with the elevation change. See details 8 and 9 on LL513 for further clarification. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 02/10/2021 |  |  |  |  | Closed | 02/17/2021 | 02/18/2021 | 02/16/2021 | 02/10/2021 | 02/10/2021
928 |  | 0 |  |  | Request for Information | Hardware Review Questions | Openings 013, 043A, 048 and 123 are hollow metal doors that call for a 253 door bottom (see attached cut sheet). With the channel on the bottom of hollow metal doors, these will not work. can a surface mount be used? Currently opening 013A, hardware group 11 (attached), does not call for a closer. Should it have one? Should opening 076 have custom hardware? currently it calls for standard hardware in set 33. I believe it should match opening 074 and hardware group 064. Hardware groups attached. Please confirm lock and closer function on opening 191. The is the exterior gardener restroom. Currently the lock function is a classroom function. If it was changed to an entry function, there would be a button on the inside to lock the door from the inside. The closer call for a cush (stop) arm, it appears a wall stop could be used. Openings 208, 209, 210, 211A, 211B, 211C, 211D, 211E, 212, 213A, 213B, 218, 408A and 408B call for hardware group 55 (attached). the hardware group only calls for 3 ea. hinges. These are 10’ tall doors, we should change the quantity to 5 ea. hinges. |  | answers to questions: 1. Surface mounted sweeps on the doors referenced in this question is acceptable 2.Yes, door 013A should have a closer 3.Yes, door 076 should have deco hardware, matching door 074 and hardware group 064 4.Proposal to use an entry lockset on door 191 is acceptable. use of wall stops also acceptable 5.the 10' doors probably should have more than 3 hinges each.......although the historical 10' doors do only have 3. this is likely a conversation that needs to take place between the sub, Westland, Fetzers, CRSA and the owner before a decision can be made. Please try to set up a quick meeting for this. |  |  | Medium | Russ Farley | Architectural Building Sup | CRSA ARCHITECTURE |  | 02/10/2021 |  |  |  |  | Closed | 02/17/2021 | 04/12/2021 | 04/12/2021 | 02/23/2021 | 02/10/2021
929 |  | 0 | 220000 | P101 | Request for Information | Annex Level 1 restroom 134 and 152-Hose Bib Requirements | Drawing P101, level 1 Annex water distribution page currently does not appear to call out for a fixture HB-1 under lavatory at restrooms 134 and 152. All other restrooms on this floor appear to indicate hose bibs serving them. | Please confirm that no hose bibs are required at restroom 134 and 152. | Per Utah amendment to the plumbing code, hose bibs are no longer required in restrooms as long as there is an elastomeric seal in the floor drains (which is the case for this project). The hose bibs may still be provided in these 2 restrooms if the owner decides to add them. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/11/2021 |  |  |  |  | Closed | 02/18/2021 | 02/16/2021 | 02/16/2021 | 02/11/2021 | 02/11/2021
930 |  | 0 |  | ES201 | Request for Information | CCD121r1 Brides Exit Lighting | Please reference the attachment and address the following questions: 1. Provide elevation and distance from door frame do we need to place the (2) WS-X1 lights? 2. Provide a detail for mounting these BL42A on the suspended walk? |  | ¦ CRSA please provide dimensions per comment from David Tibbitts |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/11/2021 |  |  |  |  | Closed | 02/18/2021 | 03/25/2021 |  | 03/02/2021 | 02/11/2021
931 |  | 0 |  |  | Request for Information | Can Light vs. Truss clashes Annex Rooms 103, 106, 109 | How can the lighting layout be modified to avoid clashes between can lights and trusses in rooms 103, 106, and 109? Also, what are the two devices indicated in green in "Annex Foyer 103.." attachment? | The following are our suggestions: Foyer 103 - Change the rows of can lights from 6'-2 1/4" and 6'-3" from center to 5'-4" from center. Also make the other indicated dimensions symmetrical. See Attachment "Annex Foyer 103...". Hall 106 - Eliminating the can lights would be a problem as they supply emergency egress lighting. Lowering the ceiling would be a problem because of the windows. Our suggestion is to add (2) more can lights for a total of (4), and place them in a rectangular pattern as shown on attachment "Annex Hall 106..." Annex Marriage Waiting 109 - Our suggestion is to put all (4) cans in a row at 5’–6” off of center north and south instead of having (2) 5' from center and (2) 6' from center. This would avoid the trusses and keep things symmetrical. See attachment "Annex Marriage Waiting 109..." | Please refer to ASI 101 for updated light locations. ¦ ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/12/2021 |  |  |  |  | Closed | 02/19/2021 | 02/23/2021 | 02/19/2021 | 02/19/2021 | 02/12/2021
932 |  | 0 | 230000 | CCD#28R3 M100 | Request for Information | CCD#28R3 Fire Wrap Requirements | Drawing M100, CCD#28R3, Sheet note 13 indicates to install fire wrap to maintain sheer wall integrity from fire damper to low return grille on level 1 at 4 locations. Due to the time frame of the CCD28R3 being issues, the modeling and fabrication of the mechanical system per previous design had already taken place. This did not allow rooom for the fire dampers to be installed in the basement of the annex. The fire dampers are currently installed in duct risers from basement to level 1 with the dampers at the floor elevation. Also, there is currently not enough room in the vertical concrete openings to allow fire wrap to be installed around the duct as these concrete walls were poured before the CCD#28R3 was issued. | Please advise if it be acceptable to use a rock wool and fire caulk system around the duct riser on level 1 at floor height to keep fire separation between the basement and level 1 at Annex. See attached photos and marked up drawing for clarity. | Either rock wool or 5/8" gyp board with fire caulking could be acceptable. The issue is that the 1-hour fire resistance rating is maintained for the concrete wall. Verify with the architect which method is preferred before final installation. ¦ Please use 5/8" Gypsum board and fire caulking around the penetrations. ¦ ¦ Please advise if one of these installation methods is preferred? |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/12/2021 |  |  |  |  | Closed | 02/18/2021 | 03/10/2021 | 03/09/2021 | 03/02/2021 | 02/12/2021
933 |  | 0 | 220000 | MP101 | Request for Information | CCD#28R5-Condensate serving room 123 FC-1 | Drawing MP101, CCD#28R5, security room 123, does not appear to indicate any condensate piping serving HVAC unit FC-1. | Please provide pipe sizing, routing and if a condensate pump is needed. | Please refer to CCD-138 for the routing of the condensate piping. A condensate pump is not required. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/12/2021 |  |  |  |  | Closed | 02/18/2021 | 03/10/2021 | 03/05/2021 | 02/15/2021 | 02/12/2021
934 |  | 0 |  |  | Request for Information | Millwork Guard rail | ASI 66R1 change hand rail and guard rail to Cherry lumber at all wood stairs. Does this ASI apply to the guard rail in Instruction room 219, 318, Study 508, and stair lobby 501 or do all these guard rail remain paint grade? |  | Mahogany or Cherry is acceptable for all handrails, as long as it matches the standard cabinet stain throughout the project. Please use the same wood in the same area. ¦ where paint grade is specified, provide paint grade. ¦ ¦ We have received further information on this question from Paul Burningham he said; "Historically the guard rails and hand rails are paint grade at the stairs and railings on level 4. Drawings are approved as paint grade guard rails at all windows at the following rooms 219, 318, 518, and 501. The question being asked is should the guard rails in the rooms change to match the grand stair and be cherry or should they remain the historical look and remain paint grade." |  |  | Medium | Paul Burningham | Fetzer`s Inc. | Interior Designer |  | 02/13/2021 |  |  |  |  | Closed | 02/20/2021 | 03/10/2021 | 03/02/2021 | 02/15/2021 | 02/13/2021
935 |  | 0 |  |  | Request for Information | West Wall Door Way entrance | Due to Wayne and Brents onsite review on 02-15-2021. Please confirm that the West wall entrance is to be poured in 3-3’ sections as shown on sketch #3 option #2. We have already added the cross members shown in sketch #1 option #2 and will leave them there for added stability. I have added the sketches for your reference. |  | Confirmed by ARW Engineers that this matches the discussion between Brent White and Wayne Rogers. ¦ |  |  | High | Stormy Carlisle | Innovative Concrete LLC | Structural Engineers |  | 02/15/2021 |  |  |  |  | Closed | 02/18/2021 | 02/15/2021 | 02/15/2021 | 02/15/2021 | 02/15/2021
936 |  | 0 | 220000 | PS100 | Request for Information | Exterior Drinking Fountain DF-2, DF-3 color selection | Please review attached cover sheets from submittals for outdoor drinking fountains DF-2 and DF-3. Please verify the desired color of pedestal bases and finish of bowls and bubblers for each. | Provide color and finish selections, see attached submittals and drawing PS-100 for locations. | Response is attached ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Landscape Architects |  | 02/15/2021 |  |  |  |  | Closed | 02/18/2021 | 03/03/2021 | 03/02/2021 | 02/15/2021 | 02/15/2021
937 |  | 0 |  |  | Request for Information | Specification Questions for 102800 - Bath Accessories | There are lots of questions regarding the toilet and bath accessories for the St. George Temple. I’ve numbered the items I have questions about on the attached specification. 1. Bradley #5224 toilet paper holders are as cheap as they come and have controlled delivery. I’ve never supplied these for a temple before. Suggested models: Bradley #522 or #5402; Bobrick B4288. 2. These units are huge, and require holes cut through the partition panels in cases where they’re designed to serve two compartments. This would be a mistake given that the partitions are marble. Again, I’ve never supplied these for a temple before. Suggested models: toilet paper holders, see above; feminine napkin disposals, Bradley #4781, #4722; Bobrick #B270; toilet seat cover dispensers, Bradley 5831 or Bobrick B4221. Also, the plans show individual toilet paper holders and feminine napkin disposals; toilet seat covers are not shown. 3. This Bradley model (#1985) is designed to be recessed in the wall behind the mirrors. They need to be installed before the drywall, which presents a bunch of problems. Not only have I never supplied these on a temple, I’ve never supplied these anywhere! The plans appear to show surface mounted units. Suggested models: Bradley #2441 at small restrooms, #234 at larger restrooms; Bobrick B43944 at larger restrooms. 4. I would suggest one feminine napkin vendor at every women’s restroom with toilet stalls. 5. I’ve never encountered this product until now. Not shown on the plans. 6. I’ve never supplied these for a temple before. They aren’t real durable in my experience. Not shown on the plans. 7. Shower curtains and rods are typically provided by the drapery sub-contractor. 8. These are not shown; ADA dressing compartments show fixed wood benches mounted to the floor, so I’m not sure where these would be needed. 9. These are not shown on the plans. Recommendation: one per Family Assist Restroom. 10. Typically supplied and installed by the plumber. If you could have the architect address these items I think it would save everyone time and money. Given the disparity between the plans and the specs, there’s really no way to quote a price on this scope, without dozens of qualifications. I think it better to get things clarified up front than to go |  |  |  |  | High | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/15/2021 |  |  |  |  | Closed | 02/22/2021 |  |  | 02/15/2021 | 02/15/2021
938 |  | 0 |  |  | Request for Information | Mechanical Pit Wall Finish | See Attached. What finish would you like on the mechanical pit wall? (stucco, EFIS, painted white) |  | See CCD-134 sent 2/26/21. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/16/2021 |  |  |  |  | Closed | 02/23/2021 | 03/10/2021 | 03/09/2021 |  | 02/16/2021
939 |  | 0 |  |  | Request for Information | 500 South site access and gate stop | 1. The gate on 500 south is an entry point to the property. If this gate is open for site access should bollards be installed? If so please provide direction to install before fire lane is poured. 2. There is no way to secure the gate when it is open. See attachment for possible solution. |  | See attached, updated detail for the drop rod anchor detail. See CCD 139 for additional bollard locations. |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 02/16/2021 |  |  |  |  | Closed | 02/23/2021 | 03/18/2021 | 03/13/2021 | 02/17/2021 | 02/16/2021
940 |  | 0 |  |  | Request for Information | Room 318 Floor Boxes Clarification | Can the plans (EP103; AE4305 B1, B3, B4) be modified to show that the outlets and data in room 318 are floor boxes, not wall boxes? In following the direction received from CRSA in RFI 787 we went ahead and installed floor boxes in room 318. In a later RFI (863) the floor boxes in rooms 317, 319, 517, and 519 were changed to wall boxes cut into the plaster. This appears to have led to some confusion. Please see attached drawings. Also, per direction received in RFI 815 and CCD 118, the WAP in room 318 was moved from the ceiling to the center of the west wall. Can this change be reflected on EP103 and AE4305? Again, please see attached drawings. |  | We will change the devices in 318 back to floor boxes. Updated electrical drawings will be issued a part of ASI#96. This will include a complete electrical set of drawings. ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/17/2021 |  |  |  |  | Closed | 02/24/2021 | 02/23/2021 | 02/18/2021 | 02/18/2021 | 02/17/2021
941 |  | 0 |  |  | Request for Information | Historic - HVAC Penetrations at East Spiral Stair Chases | Please provide a detail showing how to frame out HVAC wall penetrations at the spiral stair chases. Some existing 4x4 members will need to be cut at various locations to create these openings and will require a fix. See attached photo of existing framing. Penetrations locations have been laid out in the field for site review. |  | Please see attached for recommended framing around the penetrations ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 02/17/2021 |  |  |  |  | Closed | 02/24/2021 | 02/25/2021 | 02/24/2021 | 02/19/2021 | 02/17/2021
942 |  | 0 |  |  | Request for Information | Site Lighting Finish Selection | See attached transmittal letter for the color chip samples. Please provide color (finish) selection for the following lights: BL42A, EP10A, EP12A, EP12B, PA18A, Camera Pole, EFA, EFB, EFC, EFE, EFF, EFG, EFH, LF3A, IR7A, IR7B, SL9X3A, SW3A, SW7A. |  |  |  |  | Medium | David Barney | Wilkinson Electric Inc | Westland PE’s |  | 02/17/2021 |  |  |  |  | Closed | 02/24/2021 |  |  |  | 02/17/2021
943 |  | 0 |  |  | Request for Information | Site fence stem wall paint | The concrete stem wall on the existing site fence is painted a grey color that matches the existing color of the metal fence. Do the concrete stem walls need to be painted a different color? If so what color should they be painted? |  | We would prefer that none of the stem walls have paint on them. The existing stem walls need to have the paint removed. After they have been sandblasted (or by whatever removal method is the most effective) we will need to evaluate their condition and determine if their appearance is acceptable. If they do not meet the quality standards, a paint color will be selected. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 02/17/2021 |  |  |  |  | Closed | 02/24/2021 | 03/10/2021 | 03/04/2021 | 02/18/2021 | 02/17/2021
944 |  | 0 |  |  | Request for Information | Score joints @ 4" concrete curb wall | Sheet LL501 detail 7 (attached) calls out for score joints 10' O.C. hand tooling these joints requires stripping the forms before the mud would be fully set. This may result in an end product that would not be acceptable. We have proposed a 1/4" saw cut joint 10' O.C. on the 4" or 6" curbs with the same condition. We believe this will result in a much better finish and accomplish the same result. Please set this at high priority as we will begin pouring the 4" curbs at the fire lane Feb. 22 |  | Using a 1/4" sawcut joint is acceptable. Match sawcut joint with bevel detail from walkway. Align joints in curb with the joints in the walkway. ¦ |  |  | High | Stormy Carlisle | Innovative Concrete LLC | Landscape Architects |  | 02/18/2021 |  |  |  |  | Closed | 02/21/2021 | 03/05/2021 | 03/05/2021 | 02/18/2021 | 02/18/2021
945 |  | 0 |  |  | Request for Information | Electrical outlet locations for east plaza area | Related Scope: Electrical/Landscaping Related Documents: ES101/LL100 Description: Electrical outlet locations · Green cloud, confirm that the desired location for these outlets are in sod areas · Blue cloud, confirm these outlet locations are to be centered behind benches |  | Please adjust the locations according to the attached pdf. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 02/18/2021 |  |  |  |  | Closed | 02/25/2021 | 03/10/2021 | 03/09/2021 | 02/18/2021 | 02/18/2021
946 |  | 0 | 220000 |  | Request for Information | Restroom 152 clear space dimensions | CCD#128, restroom #152 appears to have omitted the dimensions for the marble partitions. It has been discussed on-site that the marble material is to be 3/4" in thickness. | Please confirm the thickness of the partition material to allow for correct water closet layout of WC-1 and WC-2. | Confirmed. Partitions are 3/4" thick with 36" clear at each stall. Center toilet in stall. The remaining space will be added to the ADA stall on the North where the toilet is 18" off the North wall. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 02/18/2021 |  |  |  |  | Closed | 02/25/2021 | 03/23/2021 | 03/19/2021 | 02/23/2021 | 02/18/2021
947 |  | 0 | 220000, 230000 | MP101 | Request for Information | Fan Coil FC-EV-2 at lobby 131-Missing Piping | Drawing MP101, elevator lobby 131, fan coil unit FC-EV-2, appears that no hydronic chilled piping or condensate piping is shown serving this unit. A previous RFI #250 answer indicated that pipe routing would be included in CCD#038. It does not appear to have been included. | Please provide chilled hydronic and condensate pipe routing to serve the FC-EV-2 mechanical equipment. Note that modeling of this area has been completed and might require re-visiting of this area to accommodate this piping. See attached marked up drawing for reference. | Refer to CCD-138 for the chilled water pipe routing to FC-EV-2. |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/19/2021 |  |  |  |  | Closed | 02/26/2021 | 03/10/2021 | 03/05/2021 | 02/23/2021 | 02/19/2021
948 |  | 0 |  |  | Request for Information | Lighting 026,027 | There are 2-Type LS4C lights in each restroom(026,027) we need location dimensions for both (See Attachments please advise) |  | The LS4C fixtures should be Ceiling-Mounted, 6" from the Toilet Wall in the locations indicated on the Attached Drawings. ¦ please see response from dave tibbitts ¦ Kyle and Scott, See comments in RFI and email from David T on 4/13 with two possible alternate fixtures to use in lieu of the basic wrap around LED light that was submitted by Wilkinson. The recessed fixture is most likely the better aesthetic option however it may have a larger impact on ceiling framing/cost. David T. can provide additional feedback and fixture recommendations if needed. | CRSA ARCHITECTURE |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/06/2021 |  |  |  |  | Forwarded | 03/02/2021 | 03/17/2021 | 03/16/2021 | 04/15/2021 | 02/23/2021
949 |  | 0 |  |  | Request for Information | Data & Outlets at Pulpits 4th Floor | On the 4th floor room 408 there are outlets and data shown at the two upper tiers of pulpits on each end. At the west end under the benches of the A. P. pulpits there are air return grills where floor boxes would be installed. | There is a better location to cut the boxes in under the benches in the lower face of the pulpits that puts the boxes and conduit in the space under the rostrum. See the attached drawings. | Envision is OK with the outlets being installed in this location. ¦ See response from CRSA and Envision Engineering. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/24/2021 |  |  |  |  | Closed | 02/27/2021 | 03/10/2021 | 03/09/2021 | 02/25/2021 | 02/23/2021
950 |  | 0 |  |  | Request for Information | Lvl 4 Barrel Ceiling Sub-Straight | Direction for the barrel ceiling on level 4 as plaster substrate looks to be subpar and is cause for concern with R. Phillips Plastering. Please advise if the plaster should be removed then replaced with new? Clint with R. Phillips has mentioned that he could install some wire mesh then refinish but at that point he is concerned about the added weight that the new system would add to the existing plaster attachments. |  | It is acceptable to add up to 3psf of additional plaster weight to the existing ceiling. The new plaster overlay will need to weigh less than 3psf if it is to be applied to the existing ceiling. Attachments of the existing plaster ceiling should be reviewed and upgraded as necessary to support the additional overlay weight as well. ¦ Please see response from ARW. PR #14 has been sent out to get pricing and options for the owner and design team to review. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/23/2021 |  |  |  |  | Closed | 03/02/2021 | 03/09/2021 | 03/09/2021 | 02/23/2021 | 02/23/2021
951 |  | 0 |  |  | Request for Information | Electrical Penetrations at Existing Concrete Wall A2 and AG | Please see the attached layout of (6) 5” electrical penetrations to be made at the south wall of TFM shop 042, grid A2 and roughly grid AG. The wall was scanned and penetrations were laid out so that no vertical rebar would be cut. The spacing between the penetrations is roughly 16” OC. Please advise if this is acceptable. Also, these penetrations will sit below the new gas meter and gas meter concrete pad. Please advise what the clearance requirements are. |  | The proposed locations are acceptable from a structural standpoint. We recommend that a minimum of 8" of soil be placed between the bottom of the concrete pad and the top of the electrical conduit, but this recommendation needs to be checked and verified with the electrical engineer. ¦ Envision is Ok with the locations proposed as long as they provide the proper sleeve/seals through walls and rigid metal conduit as the conduit passes through to exterior locations to avoid shearing off conduit during any soil settling. These are requirements all indicated in the specifications they will need to reference. They will need to coordinate with gas meter and gas piping to avoid any conflicts of that system as well. ¦ ¦ Please advise if the solution by Zach Hansen will be acceptable? |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Electrical Engineers |  | 02/23/2021 |  |  |  |  | Closed | 03/02/2021 | 03/02/2021 | 03/02/2021 | 02/25/2021 | 02/23/2021
952 |  | 0 |  |  | Request for Information | 4th FLR pulpits exterior outlets | Are the dimensions we propose acceptable for installing the outlets in the 4th floor pulpits outside walls? See attachments | Install the outlets in the West pulpits' outside walls at 15 1/2" AFF to keep the box underneath the rostrum floor in the dead space, and 31" from West wall. Realistically, 15 1/2" is the maximum height these can be installed at. Install the outlets in the East pulpits' walls at 18" AFF and 27 1/2" from East walls. Or, match the 15 1/2" installation height of the West pulpits. Please see the attached drawings. | Envision is Ok with the outlets being installed lower as long as the lowest outlet will still meet the ADA required height above 15". All (4) outlets may be installed at the same height. Dimensions from the wall are flexible to allow for code required heights of installation. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | Electrical Engineers |  | 02/23/2021 |  |  |  |  | Closed | 02/28/2021 | 03/02/2021 | 03/02/2021 | 02/24/2021 | 02/23/2021
953 |  | 0 |  |  | Request for Information | Hardware Color | Please confirm if the hardware is called out as being all Brass with the exception of the Bronze door witch will be all brass with the exception of a two tone Brass and Bronze handle? |  | Where two-tone is specified use Bronze accessories such as hinges, closers etc. Where Brass is called out use Brass accessories such as hinges, closers etc. ¦ |  |  | High | David Adams | Westland Construction, Inc. | Interior Designer |  | 02/23/2021 |  |  |  |  | Closed | 02/26/2021 | 02/24/2021 | 02/23/2021 | 02/23/2021 | 02/23/2021
954 |  | 0 |  |  | Request for Information | Clarification Questions Glass a Font | How far to extend the glass? Currently I intend the etched glass to extend to line up with the end of the platform. However, this does not obscure from all angles within the font. To obscure from all angles within the font I think almost half of the glass would need etching. Is the intention to have it on the wet side only? What do we need to do to plan for the view screen? Currently there is a note to remove one baluster to not impede the screen. Do we need to triangulate an unetched region of the glass to not obscure the view screen as well? What about the stair cases? A privacy screen does not obscure anything on either staircase. For reference I have linked this RFI to a Submittal showing the etched pattern to be used at the font. |  | OAC on 3-18-2021, Chris instructed the design team to NOT proceed with any privacy screen at the font. We will still have the glass splash guard, just no etching. ¦ |  |  | Medium | Steve Brown | Historical Arts & Casting Inc. | CRSA ARCHITECTURE |  | 02/24/2021 |  |  |  |  | Closed | 03/02/2021 | 03/23/2021 | 03/19/2021 | 02/24/2021 | 02/24/2021
955 |  | 0 |  |  | Request for Information | 4th floor barreled ceiling speaker/strobe dimensions | Can we get dimensions for the layout of the Speaker Strobes on the barreled ceiling of the 4th floor Assembly Room 408? | We propose that the 3 Speaker Strobes be centered between the existing historic medallions (or as close to centered as the ceiling truss framing allows) as shown on the attached drawing. Please advise. | Please locate strobes to be centered between medallions as per locations shown on the redlined drawing attachment from Wilkinson's Electric. ¦ |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/24/2021 |  |  |  |  | Closed | 02/28/2021 | 03/10/2021 | 03/09/2021 | 02/25/2021 | 02/24/2021
956 |  | 0 |  |  | Request for Information | Rebar Questions Detail 13 on S203 | There are a few revisions/adjustments that we are requesting on the rebar in this area. Please see the attachment for illustrations. First the width of the bars that were epoxied into either side of the wall at the Header area. Rod with AGEC requested an additional 4’ bar be placed to help splice the bars that are overlapping. Do you take any issue with this? The rectangle bent bar inside header area. Innovative does not have the exact manufactured bar for this are but wanted to know if their proposal would be allowed. Last item is on doorway 064a and 063a from the confirmation rooms into the Stairs. The stairway wall is a radius wall. How do we need to adjust for the radius change? Will we need to have our bar follow the profile or will it be allowed to have the thickness of concrete be closer to the rebar in the center? Is there a minimum or maximum thickness of concrete? | Question #1 Response – Yes. Please add a full length bar as suggested. Question #2 Response – Using Innovative’s proposed configuration is acceptable provided that the length of splice between the two U bars is at least 29”. Question #3 Response – The bar can be straight and does not need to follow the radius of the curved wall. The minimum clear distance of the bar to the outside face of concrete at the inside of the curve needs to be 1-1/2” clear. | We confirm the Suggestions are correct. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 02/25/2021 |  |  |  |  | Closed | 03/03/2021 | 02/25/2021 | 02/25/2021 | 02/25/2021 | 02/25/2021
957 |  | 0 |  | S202 | Request for Information | Structural Support at HVAC penetrations Level 0.5 | At floor deck openings for level 0.5, what conditions need to be met in order to allow us to block out and add reinforcing versus using detail 12/S202? | Please confirm; Per our structural note H.3, openings exceeding 6” in size need to be supported per 12/S202. The penetrations clouded in green on your attached drawing will require frames around them. There is some leniency with the size of the hole and we can help address that on a case by case basis if needed. In general, our rule of thumb is that the penetration can’t cut more than one deck down flute or up flute before reinforcing needs to occur. | Confirmed that the suggestion is correct ¦ Please confirm |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 02/25/2021 |  |  |  |  | Closed | 03/03/2021 | 02/25/2021 | 02/25/2021 | 02/25/2021 | 02/25/2021
958 |  | 0 |  |  | Request for Information | Drawing Clarifications Lighting Locations | Please provide the dimensions for lights in the following details. 1. AE4134 Detail B3 a. We need dimensions for vanity light. 2. AE4135 Detail B3 a. Dimensions for strobe 3. AE4127 Detail A3, B3 a. Need elevation for sconce lights. 4. AE4105 Detail B4 a. Outlet next to diffuser is to close. Please provide alternate location. |  | 1a. 1'-5 1/4" from North Wall (center with vanity plumbing), 7'-10" above finish floor 2a. 5'-0" from West Wall, 6'-8" above finish floor 3a. Both detail A3 & B3 sconce to be 5'-6" above finish floor 4a. Both detail A4 & B4, offset outlet to side of diffuser. Detail A4 shows this to be 10", if that is still not enough room it is acceptable to shift an additional few inches. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 02/25/2021 |  |  |  |  | Closed | 03/03/2021 | 03/17/2021 | 03/15/2021 | 02/25/2021 | 02/25/2021
959 |  | 0 |  |  | Request for Information | Architectural Grill Attachment | I have been informed that there could be a new attachment method. Please provide an updated attachment method for the architectural grills. For reference I have attached some photos of the possible solutions provided by our mechanical contractor. |  | Refer to detail 15/M503 that will be added as part of CCD-138. This detail will cover an alternative attachment method that will allow for the flange on the back of the decorative grilles to be eliminated, thus solving the problem of the scorch marks from the welding process. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Mechanical Engineers |  | 02/25/2021 |  |  |  |  | Closed | 03/04/2021 | 03/09/2021 | 03/05/2021 | 02/25/2021 | 02/25/2021
960 |  | 0 |  |  | Request for Information | 4th floor Exit Sign Height differences | We installed the back boxes for the exit signs in the 4th floor Assembly Hall following the dimensions given on page AE4405. Doing so put the bottoms of the East Exit Signs 4" above the tops of the transom window arches, and the bottoms of the West Exit Signs 11" above the tops of the transom window arches. Is this acceptable? | Our suggestion is to put the bottom of all of the exit signs mentioned in this RFI 4" above the tops of the arches. It is further suggested that the 4" clearance be consistently maintained above the door casework in Study 410, and Vestibules 409 and 411. There are similar doorways (221D, 220C) leading East from the Celestial Room 218 into the vestibules 220 and 221 that have Exit Signs. Should we install those two Exit Signs 4" above the arches as well? Please see attachments and advise. | Please place exit signs so bottom of sign is 4" from the arched casings. ¦ ¦ CRSA please see comment from David Tibbitts and provide dimensions. |  |  | High | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 02/25/2021 |  |  |  |  | Closed | 03/04/2021 | 03/10/2021 | 03/09/2021 | 03/02/2021 | 02/25/2021
961 |  | 0 |  | AD100B, AE4025 | Request for Information | Level .5 Chapel Window Seal | Please advise if the Window shown in the attached picture needs to be replaced. This item is time sensitive and we would like to include this in a concrete pour that will be done on the 8th of March. |  | Yes, This is a new window provided by Re-View windows. See Sheet AE100B which call this out as Type H8 (AE644). If concrete is required to repair or size the rough opening, the Head, Jambs, and sill should all be repaired following structural detail 17/S245. The rough opening dimensions have been provided on Re-Views shop drawings for window Type H8. (see attached PDF's for quick reference) ¦ Our recommendations are as follows: 1- Clean the existing stone window sill to remove any paint, dust, dirt and other latent or loose material. 2- Apply a chemical bonding agent to the stone window sill to allow bonding of the new concrete sill to existing stone. 3- Use a concrete filler material that has no large aggregate. We recommend something similar to a high strength leveling compound. f'c=5,000psi. ¦ ¦ ¦ I can’t see the information on the window seal in detail 17 on sheet S245 if it is there please advise. We are coordinating the window size with the opening and don’t see the need for infill at this location. The portion that needs to be infilled is 2” at the base of the window. |  |  | Medium | David Adams | Westland Construction, Inc. | Zach Hansen | ARW ENGINEERS | 02/26/2021 |  |  |  |  | Closed | 03/05/2021 | 03/01/2021 | 03/01/2021 | 03/01/2021 | 02/26/2021
962 |  | 0 | 230000 | M sheets | Request for Information | CD-6 Ceiling diffuser finish type | HVAC ceiling diffuser CD-6 located at the level 4 barrel ceiling assembly room, approved submittal indicates finish to be 26-White. | See attached reviewed submittals. please confirm that the 26-White finish is to be used at the assembly room location. |  |  |  | Medium | Justun Bylund | US Mechanical LLC | Westland PE’s |  | 02/26/2021 |  |  |  |  | Closed | 03/05/2021 | 03/03/2021 |  |  | 02/26/2021
963 |  | 0 | 230000 | M101 | Request for Information | RFI# 648 response-Vestibule 131 elevator fire dampers | RFI# 648 response dated 9-3-2020 indicated that new fire dampers would be added to the duct serving the elevator adjacent to vestibule 131 in the forthcoming CCD#28R3 scope. Upon receipt of CCD#28R3 it appears that these dampers were NOT included within the scope change. See attached RFI response and drawing for reference. Please advise if the fire dampers are required per the previous RFI# 648 response. |  | The missing fire dampers will be added as part of CCD-138. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 02/26/2021 |  |  |  |  | Closed | 03/04/2021 | 03/10/2021 | 03/05/2021 | 03/01/2021 | 02/26/2021
964 |  | 0 |  |  | Request for Information | Step Light SL9X3A | See two attachments. Step Light SL9X3A has a new listing in the fixture schedule of CCD-121R1. This step light has already been submitted and reviewed. Are we to resubmit on this new manufacturer/catalog number? |  | Per direction given by Scott (CRSA) please provide a submittal for the new step light. Thanks, |  |  | Medium | David Barney | Wilkinson Electric Inc | Westland PE’s |  | 03/01/2021 |  |  |  |  | Closed | 03/08/2021 | 03/01/2021 | 03/01/2021 |  | 03/01/2021
965 |  | 0 |  |  | Request for Information | Site fence elevation / Annex mechanical room | Related Scope: Landscaping / Civil / Hardscape Related Documents: LL100 / LL512 Description: The west fence that attaches to the Annex has a conflict with the mechanical room that is below this portion of the fence. The elevations detailed in LL 512 for this portion cannot be achieved do to the concrete for the top of the mechanical room shown in AE 101. I have given estimates in elevations and from what I can tell it is .80 higher than the plans show to install the fence. The mechanical room effects detail 2 and 3 of the fence on LL 512. Provide direction and elevations that avoid the current mechanical room roof conflict. |  | We have reviewed the basement section and fence. Per slab elevations shown on the attached AE101, AE301, and LL512 it appears there is no conflict, see attached and let us know if there is more to review. ¦ | Zac Givens | Westland Construction, Inc. | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 03/01/2021 |  |  |  |  | Responded | 04/15/2021 |  | 04/12/2021 | 03/03/2021 | 03/01/2021
966 |  | 0 |  |  | Request for Information | Dome Adhesive | When we detached the dome from the tower this week we found it was glued down to the wall fiberglass pieces. Do we want to use adhesive while reinstalling the dome? If so will you please give a direction on what product we should use to perform this task? This would need to be installed both above and below the new flashing piece. This was also the case with removing the spire. |  | Structurally, we care that the dome is bolted down in a similar fashion to before and aren’t relying on the adhesive to do any of that load transfer. We only care about the bolts. The adhesive was likely more for waterproofing or sealant purposes instead of helping hold down the dome. CRSA or a fiberglass/waterproofing expert should weigh in on this to make sure waterproofing and things are taken care of properly. ¦ This was answered on site and dome is already reinstalled. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/01/2021 |  |  |  |  | Closed | 03/08/2021 | 03/17/2021 | 03/15/2021 | 03/01/2021 | 03/01/2021
967 |  | 0 |  |  | Request for Information | Lighting at Hall o23A | Due to some conflicting dimensions please confirm the locations on the attached sheet are correct (see attachments please advise). If these are not correct, please provide some revised dimensions. |  | Please see attached, with responses to redlines. contractor to please note that this is likely to be a recurring issue and the instructions provided here are likely to apply elsewhere. ¦ please disregard attachment 'AE4106-RM 110-chapel' please see newly attached drawing 'AE4016-RM 023 hall' ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/01/2021 |  |  |  |  | Closed | 03/08/2021 | 03/22/2021 | 03/17/2021 | 03/01/2021 | 03/01/2021
968 |  | 0 |  |  | Request for Information | Level 5 Steel Sleeve for HVAC Opening | Please see the attached document showing the location of a level 5 embed that is interfering with the install of a steel sleeve. Please advise 1. Due to the embed blocking the path of the steel sleeve would it be acceptable to install a C-Channel above the HVAC opening? 2. Another option would be we could use the same gage of Steel plate and have it extend past the edge of the opening to a predesignated length (2')? If we can't use a C-Channel/Plate, please advise as to the install of the West side sleeve? |  | Use of a channel above the opening is acceptable. ¦ |  |  | High | Will Brimhall | Glassey Steel Works, Inc. | Structural Engineers |  | 03/01/2021 |  |  |  |  | Closed | 03/04/2021 | 03/03/2021 | 03/03/2021 | 03/01/2021 | 03/01/2021
969 |  | 0 |  |  | Request for Information | Rotted Boards in Dome | The vertical boards running around the tower wall can all be removed without consequence. The horizontal boards however are backing for the fiberglass wall pieces below. There is sufficient rot in these boards and will need to be removed. | Install treated plywood in place of the horizontal boards. Per our phone conversation, we take no issue with the treated plywood substitution. Please use treated plywood that is a minimum 23/32” thickness. | Confirmed. ¦ |  |  | Medium | Josh Nay | Westland Construction, Inc. | Structural Engineers |  | 03/02/2021 |  |  |  |  | Closed | 03/08/2021 | 03/03/2021 | 03/03/2021 | 03/02/2021 | 03/02/2021
970 |  | 0 |  |  | Request for Information | Sealing Rm 3 Data & Outlets | The North, East, and South walls are being furred out 1 1/2", and the West wall has a thick layer of plaster being put back on. Wall sconce boxes are already being fit recessed into these walls. We would also like to install the data and outlets in the walls per previous discussion. The outlet in the northeast corner especially will be more durable and convenient if it is installed in the wall since it will be used nightly for vacuuming. Please confirm if this is acceptable. If the devices are able to be moved to the walls please provide dimensions. See attached drawing. This change would not incur any cost increase. |  | Changing floor boxes to wall mounted outlets and data in this room is acceptable as long as there is no cost change. A credit back to the owner will be expected for the difference of the floor box outlet. The outlet and data on the West wall will need to be centered in the wall between the two door openings and at standard height. The outlet in the southeast corner needs to be located to the east furred wall 16 inches off the southeast corner. Please coordinate with Jason Fullmer for clarification if needed. ¦ ¦ Envision has no issue with changing these to wall devices. Architect to provide dimensions. |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/02/2021 |  |  |  |  | Closed | 03/09/2021 | 03/22/2021 | 03/19/2021 | 03/03/2021 | 03/02/2021
971 |  | 0 |  |  | Request for Information | Drawing clarifications | rooms 123,124,125B have not been updated on electrical drawings EL101A, EP101, EC101. Could we have these updated along with any interior elevations that will change? Restroom 016 shower are appears to have an area that will be dark. we suggest adding an additional recessed can. (see attachments please advise) |  | I can't see the attachment you reference in your question. ¦ ¦ Additional information regarding what changes were mad is needed for Envision to update electrical drawings. Provide additional details on what needs to be updated and we will revise drawings. An additional lighting fixture inside the shower is not necessary. The recessed light in that side of the restroom could be centered more in the space, but should provided sufficient lighting for that area and shower. An additional light could be added if owner desires however there would likely be additional costs. ¦ Attachment added | CRSA ARCHITECTURE |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/02/2021 |  |  |  |  | Forwarded | 03/09/2021 |  | 03/31/2021 | 04/15/2021 | 03/02/2021
972 |  | 0 |  | S106, S106A | Request for Information | Framing at Level 5 Barrel Ceiling Attic | Reference sheet S106 and S106A issued in CCD 47. Chandelier support framing was provided as noted in the attached to accommodate existing medallion locations. Also, catwalk framing was provided at the west truss bay as noted in the attached to assist in HVAC install and future maintenance. Framing contractor is for team to confirm these as additions made to their scope of work and as cost changes. |  |  |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Westland PE’s |  | 03/02/2021 |  |  |  |  | Closed | 03/09/2021 | 03/03/2021 |  |  | 03/02/2021
973 |  | 0 | 000000 |  | Request for Information | Dock Rooms Electrical Revised | Please advise if the revised layout from ASI 050 or CCD 099 is accurate. This question has arisen because it is showing a data line connection being half in and out of the wall. |  | Neither one this area was most recently updated in CCD-108. But the data outlet in question was missed as being deleted in that update as well. Please remove the data outlet. ¦ See ASI #113. Per the comments below Data is relocated inside First Aid 124 ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/05/2021 |  |  |  |  | Closed | 03/09/2021 | 03/22/2021 | 03/19/2021 | 03/03/2021 | 03/03/2021
974 |  | 0 |  |  | Request for Information | Medallion Thickness dimensions A-22, A-28, D-44 | Can we get the medallion thickness dimensions for A-22, A-28, and D-44 where the electrical boxes are located in the middle? They were not included in CCD 19R5. We scaled them off but are not sure our measurements are correct. See attachment. |  | Medallion A-22 & A-28 are 1-1/2" thick at the center. Medallion D-44 is a historic (or scanned replica of historic) and will need to be field verified. This medallion can be found in Rooms 220, 221, 318, 409, 410, 411 ¦ |  |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/03/2021 |  |  |  |  | Closed | 03/10/2021 | 03/10/2021 | 03/08/2021 | 03/03/2021 | 03/03/2021
975 |  | 0 |  |  | Request for Information | Bollard Light Concrete Base Depth | Refer to the attached bollard light base detail and type BL42A bollard light submittal. The 3'-6" depth called out in the detail is much deeper than any bollard base we have ever done before. It seems that half that depth would be sufficient since none of these are "free standing" but will penetrate through the flatwork. Please confirm if this detail is correct? |  | ¦ Envision Engineering hired a Structural Engineer to design this Mounting Detail for us, so we are uncomfortable ignoring it without a Project Specific Structural Review. If CRSA wants to have the Project Structural Engineer Review the Detail and Revise it that is fine, but Envision Will Not Override the Advice of the Structural Engineer who Created the Detail. |  |  | Medium | David Barney | Wilkinson Electric Inc | Kyle Welch | CRSA ARCHITECTURE | 03/03/2021 |  |  |  |  | Closed | 03/10/2021 | 03/10/2021 |  | 03/03/2021 | 03/03/2021
976 |  | 0 |  |  | Request for Information | Bride Room #165 - North Window | Annex precast window openings do not line up with established grid lines. North exterior precast window opening in Bride Room #165 is not center in room. Please advise adjustments necessary to center window in Bride #165. |  | Instruction was provided through CRSA's field report and has been coordinated with Jay and Carter on-site. Please consult with Westland Construction. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/03/2021 |  |  |  |  | Closed | 03/10/2021 | 03/17/2021 | 03/15/2021 | 03/03/2021 | 03/03/2021
977 |  | 0 | 033000 | LL501 | Request for Information | Concrete Paving Control Joints | We purpose to hand tool the score joints where called out as "sawcut with beveled edges" per I on the material schedule (det'L 2 sheet LL502 site details). We feel the hand tooling is a cleaner more precise look and will match the 1/4" corner trowel score joints on the 4" concrete walks. Saw cutting opens the door for many errors. We also feel we can control the schedule if we hand tool the score joints. The saw cutting will most likely be subcontracted out and we will be at the mercy of their schedule. Please set this to high priority. Pours containing this detail will begin soon. Please answer by 3/12/2021 | 1/4" corner trowel to match 4" concrete walks | The preference is to maintain the joint as currently approved - using a tooled joint for the curvilinear sections of pathways around the perimeter of the site, and the sawcut/bevel joint for all straight sections. ¦ As per our review of the mockups please proceed with the hand tool for the score joints. Please also refer to the attached field report for further comments and instruction regarding hand tooling. ¦ This one is time sensitive please expedite response. ¦ Please review, respond, and consider email sent out by Ryan Thomas 3/10/2021 before closing. Thank you! |  |  | High | Stormy Carlisle | Innovative Concrete LLC | Landscape Architects |  | 03/03/2021 |  |  |  |  | Closed | 03/06/2021 | 03/29/2021 | 03/29/2021 | 03/03/2021 | 03/03/2021
978 |  | 0 |  | AE4105 | Request for Information | Exterior Porthole Windows | The porthole windows at the clerestory are out of level and not centered with gridlines. They are approximately +/- 1 in too far north. Please advise if interior and exterior framing are to follow the windows or follow the dimensional layout provided on the plans? |  | Yes, Follow the Windows. ¦ |  |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/03/2021 |  |  |  |  | Closed | 03/10/2021 | 03/22/2021 | 03/22/2021 | 03/03/2021 | 03/03/2021
979 |  | 0 |  |  | Request for Information | NORTH CONFORMATION DOOR FILL IN | Would it be acceptable to use detail 17 on sheet S245 as illustrated in the attached photo/drawing. |  | This is acceptable. |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 03/04/2021 |  |  |  |  | Closed | 03/10/2021 | 03/04/2021 | 03/04/2021 |  | 03/04/2021
980 |  | 0 |  |  | Request for Information | Annex W. Dock Garage Door Opener | There is no power (ceiling-mounted receptacle) or conduit for door safety sensors shown for a garage door opener on the West Delivery Dock. will these be needed? If so can we get dimensions for these locations? Please see attached drawing. |  | Power and conduit will be added as part of ASI-89R.4. ¦ Revision changed. Drawings issued as part of ASI-113 ¦ ¦ We will close this when we receive the ASI-89R.4 |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/04/2021 |  |  |  |  | Closed | 03/11/2021 | 03/31/2021 | 03/25/2021 | 03/04/2021 | 03/04/2021
981 |  | 0 |  |  | Request for Information | Vertical Platform Lift Wiring, Baptistry | Westland conducted a meeting on site with Westland, Wilkinson and Able Access to review the conduit routing needed for the Vertical Lift Platform. In this meeting we came up with the attached conduit routing diagram. Please advise if you see any concerns with the attached wiring diagram. Also, please advise if we should feed the power from Panel L3S1 instead of L3P1A-3 so that it still functions in case of a power outage? | Install a 4 11/16" J-box for phone and low voltage wiring towards the west side of the south wall of the Platform Lift enclosure. Install (2) conduit sleeves for door contact/latches as shown at 36" AFF. Install (2) 4" square boxes w/1-gang mud rings and conduit for call buttons as shown. Place call buttons 42" AFF to center. Install power in 4" square J-box next to low voltage J-box for power feed. | As long as what is proposed follows manufactuer recommendations and provides the complete wiring and fully operational system, Envision is OK with the suggestions noted. It is not necessary for the lift to be on stand-by power, however if it is a no cost change it could be beneficial to move it over to stand-by. ¦ We trust the electrician to find the best location for power based on current loading in the panel and note the revised circuit number in as-built info. ¦ ¦ There will be no cost in changing the power circuit to Standby. Panel L3S1 and L3P1A are in the same electrical room, so conduit and wire lengths would be essentially the same either way. There are plenty of spares in L3S1, and Phases 'A' and 'B' are currently lightly loaded. |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/05/2021 |  |  |  |  | Closed | 03/12/2021 | 03/31/2021 | 03/25/2021 | 03/05/2021 | 03/05/2021
982 |  | 0 |  | B3/AE4117 | Request for Information | HVAC wall diffuser layout RM 133 | Reference B3/AE4117. Please confirm HVAC diffusers on East wall are to be equal distance from center. |  |  |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Westland PE’s | [6 empty] | Draft | 03/08/2021 |  |  |  | 03/05/2021
984 |  | 0 |  |  | Request for Information | MEP layout at room 136 | Reference sheet AE4118. Please advise if MEP layout should be revised to be centered on walls within each partitioned section of the room. |  | CRSA agrees, Mechanical Grilles should be centered on walls within each partitioned room. ¦ ¦ VBFA takes no exception. Architect to confirm layout adjustments for the mechanical grilles in Instruction - Brother [136]. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Scott Gilberg | CRSA ARCHITECTURE | 03/05/2021 |  |  |  |  | Closed | 03/10/2021 | 03/31/2021 | 03/18/2021 | 03/22/2021 | 03/05/2021
985 |  | 0 |  |  | Request for Information | MEP layout at room 136 | Reference sheet AE4118. Please advise if MEP layout should be revised to be centered on walls within each partitioned section of the room. |  |  |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Westland PE’s |  | 03/05/2021 |  |  |  |  | Closed | 03/10/2021 | 03/08/2021 |  |  | 03/05/2021
986 |  | 0 |  | S100B, S102 | Request for Information | Historic - HVAC and Wall Type Coordination | 1) At Grid HC between Grids H1 and H2 the plans shown duct piping rising up through the wall from level 0.5 to level 2. Should the wall types at these locations and at both levels be changed to LVL walls type 90? Also, should HSS 6x2 supports as shown in 9/S222 be installed at level 0.5 at this location? 2) Reference attached sheet S100B. Please advise if detail 9/S222 should apply to the wall located at Grid HE between H4 and H5. |  |  |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Westland PE’s |  | 03/06/2021 |  |  |  |  | Closed | 03/13/2021 | 03/10/2021 |  |  | 03/06/2021
987 |  | 0 |  |  | Request for Information | Dock Security Office and Restroom device dimensions etc... | Can we get a dimensioned layout on the elevations page for the faucet power J-box and sink outlet in the Dock/First Aid Restroom 125B? Please provide dimensions for lighting layout in Security Office 123 and Restroom 125B. Should the lighting for the Security Office and First Aid room be on an Emergency circuit for emergency egress lighting? |  | See comments from Jessica and Kyle regarding responses to questions. ¦ Please see comments below. The lighting layout in the security office is part of ASI 96 instead of being put in an upcoming CCD. ¦ ¦ CRSA to provide dimensions requested based on current device locations in electrical model. Lighting for first aid and security office is not required to be on emergency power but could be added to the emergency circuit in the area if owner wants them on emergency power. |  |  | High | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/08/2021 |  |  |  |  | Closed | 03/11/2021 | 04/01/2021 | 03/31/2021 | 03/09/2021 | 03/08/2021
988 |  | 0 |  | EL102A, EL102B | Request for Information | Level 2 Chandelier Locations | Please provide Dimensions for the locations of the level 2 Chandeliers. This is so we will be able to get the chandeliers lifts laid out. For convenience I have included some drawings showing the exact chandeliers we have in mind. If any have been missed please include them. |  | Please see the attached 2nd level ceiling layout with notes and dimensions locating the lighting. ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/08/2021 |  |  |  |  | Closed | 03/15/2021 | 03/31/2021 | 03/29/2021 | 03/08/2021 | 03/08/2021
989 |  | 0 |  |  | Request for Information | Hall 023 Lighting Layout Dimensions | Please confirm the lighting layout dimensions used in Hall 023 for the can lights. The most commonly occurring dimension from center of light fixture LF-H2 to the center of adjacent can lighting is 2'-11 1/4". The ceiling was framed to this dimension throughout. We will disregard the dimension given placing the can lights 3" off center to the west unless otherwise directed. Please confirm if this is acceptable. See attachment. |  | Duplicate RFI, see response to RFI 967. Yes disregard 3" offset from centerline and keep everything center in ceiling. ¦ |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/09/2021 |  |  |  |  | Closed | 03/16/2021 | 03/31/2021 | 03/17/2021 | 03/09/2021 | 03/09/2021
990 |  | 0 | 220000 |  | Request for Information | Confirming partition layout at Restroom 070 Historic | The partition layout given to U.S. Mechanical by Scott Gilberg 3-4-21 is attached for women's restroom 070. The new layout will give a slightly larger handicap stall than is currently shown on the contract documents. It will also make the two smaller stalls uniform while keeping the water closets at 18" from the wall. Please confirm the new placement of partitions is accurate. | See attached screenshot for clarification |  |  |  | Medium | Justun Bylund | US Mechanical LLC | Westland PE’s |  | 03/09/2021 |  |  |  |  | Closed | 03/16/2021 |  |  |  | 03/09/2021
991 |  | 0 |  |  | Request for Information | PR_10 - Brides Skylight Details | Regarding the Brides Dressing Lockers do please provide some section details of what the profiles look like and how it integrates with the art glass? B2, B4/AE4133 shows a basic section but not a whole lot of detail. |  | See additional information for Bride's Skylight on: C1/AE312 – Annex – North/South Section A2/AE369 – Bride’s Skylight A3/AE369 – Skylight Well Wall B2/AE369 – Bride’s Skylight Detail A5/AE556 – Skylight – Cove Lighting Detail D1/AE571 – RM 165 Skylight Crown |  |  | Medium | Hyrum Ence | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/09/2021 |  |  |  |  | Closed | 03/16/2021 | 04/05/2021 | 04/05/2021 | 03/09/2021 | 03/09/2021
992 |  | 0 |  |  | Request for Information | Dock Lift Bollard RFI | See the attachment. The idea for this RFI is bollards instead of bumpers because it would add protection for the buttresses and ensure that trucks stop in the correct location to use the dock lift. |  | This was reviewed and pipe bollards at the loading dock are not wanted. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/09/2021 |  |  |  |  | Closed | 03/16/2021 | 03/31/2021 | 03/25/2021 |  | 03/09/2021
993 |  | 0 |  |  | Request for Information | OUTLET LAYOUT ROOM 133 | Reference sheet AE4117. The layout for the outlets on the north and south walls of room 133 vary by 2”. Please advise if these are to be the same distance off the east wall. |  | Yes, these outlets are to be aligned (1'-4") from East wall. Additionally an outlet was missing in the North West corner, see detail B2. This will be 1'-4" from the west wall to center of outlet. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/09/2021 |  |  |  |  | Closed | 03/16/2021 | 03/17/2021 | 03/15/2021 | 03/09/2021 | 03/09/2021
994 |  | 0 |  | EL101A | Request for Information | Hall 126 LV switch relocation | LV switch #40 that operates the lighting in Hall 126 cannot be roughed in where shown on the print. There isn't sufficient room. Please see attached pic. | It is suggested that it be relocated to the North, adjacent wall nearby. Please see attached drawing. |  |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/11/2021 |  |  |  |  | Closed | 03/18/2021 | 03/11/2021 |  | 03/11/2021 | 03/11/2021
995 |  | 0 |  |  | Request for Information | Barrel Ceiling Speaker Framing | Please provide dimensions for the speaker in the barrel ceiling. |  |  | CRSA ARCHITECTURE |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/11/2021 |  |  |  |  | Forwarded | 03/18/2021 |  |  | 03/11/2021 | 03/11/2021
996 |  | 0 |  |  | Request for Information | Annex Rooftop Exhaust Fan Circuiting | On the Annex rooftop there are 5 exhaust fans shown sharing (1) 120v 20A circuit, L2P1B-23. These are EF1-01 (2.5A), EF1-03 (8.8 A), EF1-08 (2.8A), EF1-09 (3.5A), and EF1-10 (2.2A). According to the submittals the amp draw on these fans totals 19.8 amps. This load is too high for a continuous duty load on a 20 amp circuit. | It is proposed that these exhaust fans be re-grouped as follows: EF1-03 and EF1-08 continue to be fed from L2PAB-23. EF1-01, EF1-09, EF1-10 be grouped together and fed from a circuit in L1P0C, room 040. The roof top service outlets would continue to be fed from L2P1B-21. It is not anticipated that this will incur any additional costs. Please see the attachment. | Envision sees no issue with re-routing of the circuiting as described. ¦ |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/11/2021 |  |  |  |  | Closed | 03/18/2021 | 03/11/2021 | 03/11/2021 | 03/11/2021 | 03/11/2021
997 |  | 0 |  |  | Request for Information | BP2 Dimension RFI | (See the attached) IN THE SUBMITTAL RETURNED 12-23-20, 7'-8" WAS PROVIDED FOR FLAT DIMENSION AND 4'-3" WAS PROVIDED FOR THE SLOPED. THIS WOULD REDUCE THE WALL 2" AND I NEED TO VERIFY THE 2" DIFFERENCE BEFORE I CHANGE THE LAYOUT FOR THE CONCRETE WALL ON THE PAVING PLAN. |  | See attached. |  |  | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 03/11/2021 |  |  |  |  | Closed | 03/18/2021 | 04/15/2021 | 04/14/2021 |  | 03/11/2021
998 |  | 0 | 220000 | p sheets | Request for Information | Revised Layout of Partition at Restroom 070 | Restroom 070, level .5 Historic, see attached revisions to partition layout and water closet placement for review and approval. Handicapped stall is 5' clear, two standard stalls are 3'6" clear with water closets at 1'6" to partition side of wall. Please confirm this layout is acceptable. | Review layout and approve prior to installation of plumbing piping routing and backing placement. | This layout is acceptable to CRSA ¦ ¦ VBFA takes no exception. Architect to confirm layout adjustments for restroom partitions in Restroom - Girls [070]. |  |  | Medium | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/12/2021 |  |  |  |  | Closed | 03/19/2021 | 03/19/2021 | 03/18/2021 | 03/16/2021 | 03/12/2021
999 |  | 0 | 233723 | M601 | Request for Information | Equipment Relief Hoods | Drawing M601, equipment schedule for IH and RI Hoods, keynote 3 calls for ATC Dampers to be provided, Spec Section 233723, part 1, sub part 1, paragraph 1.4 item 3-B also indicates ATC dampers to be provided. Following a review of the HVAC Control drawings, sequence of operations does not appear to indicate how these hood dampers are to be controlled. | Please provide direction as to how the hood dampers are to be controlled. See attached for clarification. | The damper for relief hood RH-1 will be controlled to modulate based on the room pressure sensor for Mech [032] where AH-2 is located. The dampers for IH-1 and IH-2 will have 2-position operation that will open when the building is in occupied mode and closed in unoccupied mode. The damper for IH-3 will also have 2-position operation but it will only open when exhaust fan EF-1-10 is running. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/15/2021 |  |  |  |  | Closed | 03/22/2021 | 03/17/2021 | 03/16/2021 | 03/15/2021 | 03/15/2021
1000 |  | 0 |  |  | Request for Information | 1000 |  |  |  | Westland PE’s |  | Medium | Camron Walker | Westland Construction, Inc. | Westland PE’s |  | 03/15/2021 |  |  |  |  | Sent | 03/22/2021 |  |  |  | 03/15/2021
1001 |  | 0 |  |  | Request for Information | Mechanical Chase 151E Firestop for conduit holes | There are good sized holes cut in the sheetrock inside of Mechanical Chase 151E on the 1st floor where the electrical conduit comes through. How should this hole be fixed in order to keep the fire stop properties? | We propose filling the space with Rockwool insulation as has been suggested and installed in other areas. See attachment for clarification. | Jason and Carter with Westland Construction informed CRSA that the building inspector per an onsite visit approved using rockwool insulation at the penetrations for this location. Wall has since been covered with Gypsum Board as construction continues. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/15/2021 |  |  |  |  | Closed | 03/26/2021 | 04/05/2021 | 04/05/2021 | 03/29/2021 | 03/15/2021
1002 |  | 0 |  | AE572/A | Request for Information | Finishes in 2nd floor instruction room benches rooms 208-211 | Please paint colors and stain finish samples for the Fixed Audience Seating LVL 2 |  | I will have these shipped out to you tomorrow midday. |  |  | Medium | Austin Gifford | Fetzer`s Inc. | Westland PE’s |  | 03/15/2021 |  |  |  |  | Closed | 03/22/2021 | 03/16/2021 | 03/16/2021 |  | 03/15/2021
1003 |  | 0 |  |  | Request for Information | Drawing clarifications | AE4002B Detail C3 A. Can light in room 16 shower area will not adequately illuminate area as placed. B. Ceiling mount occupancy sensor is not shown. 2. AE4133 Detail E!,D1,C6 (ASI 89 dated 2/3) A. Could we make all of the quad outlets 10” from wall 3. AE4113 A. There are several inconsistencies on this drawing it doesn’t appear like the electrical drawings(EP101,EL101A,EC101) were updated correctly to reflect architectural changes could we be provide correct drawings? |  | See comments from Envision Engineering below. 1A. Can light in room 016 shower is sufficient. No additional light will be necessary. 1B. Ceiling mounted occupancy sensors are not showing on the architectural Enlarged RCP drawings. Please refer to the Electrical drawings for the quantities and general locations. Align the sensor(s) with lighting and any other ceiling mounted elements. This was also discussed in our meeting with Wilkinson's on 3-31-21. ¦ ¦ Kyle, See comments from Jessica and I regarding this RFI. Let us know if you have any other questions. |  |  | High | Trask Johnson | Wilkinson Electric Inc | Kyle Welch | CRSA ARCHITECTURE | 03/16/2021 |  |  |  |  | Closed | 04/01/2021 | 04/01/2021 | 04/01/2021 | 03/31/2021 | 03/16/2021
1004 |  | 0 |  |  | Request for Information | Worker Training and Stair Lobby Dimensioned Layout | We adjusted the dimensioned ceiling layout as per walk through and conversation with Kyle Welch in the Worker Training 015 on 9 Feb. Please see the attachment for the Training Room and confirm if the noted dimensions will work. Please pay extra attention to how the speakers can lay out. Please see the attachment for the Stair Lobby 024B and noted discrepancies. Can we get a revised dimensioned layout for this area. |  | See comments and ASI-096 drawing revisions ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/16/2021 |  |  |  |  | Closed | 04/01/2021 | 04/01/2021 | 03/31/2021 | 03/23/2021 | 03/16/2021
1005 |  | 0 |  | 9/S222 | Request for Information | Level .5 Kicker Attachment | Detail 9/S222 provides attachment detail for kickers when the down of the decking runs parallel with the structural beam (North and South perimeter). However, the East and West perimeter beams run perpendicular to the downs on the decking preventing us from installing the kickers as detailed. Please see the attached sketch and let us know if this is an acceptable attachment alternative. | See Sketch | The attached alternative is acceptable. ¦ |  |  | Medium | Dan Keddington | Glassey Steel Works, Inc. | Structural Engineers |  | 03/16/2021 |  |  |  |  | Closed | 03/23/2021 | 03/22/2021 | 03/17/2021 | 03/17/2021 | 03/16/2021
1006 |  | 0 |  |  | Request for Information | Tower Truss Shoring Level 5 | Please confirm that the attached drawing is a solution that was worked out last week and that it is acceptable as it was discussed. The current shoring is in the way of installing the beam, so we needed a solution that is out of the way for install. |  | Confirmed ¦ |  |  | Medium | David Adams | Westland Construction, Inc. | Structural Engineers |  | 03/17/2021 |  |  |  |  | Closed | 03/23/2021 | 03/22/2021 | 03/17/2021 | 03/17/2021 | 03/17/2021
1007 |  | 0 |  |  | Request for Information | Security Cell Dialer and Zone Expander locations | Can the Zone Expander and Cell Tower Dialer be installed in the proposed locations? There are 32 or more security devices on the 1st floor of the Annex. Each Zone Expander will accept 16 devices, so there needs to be (2) of them for this area. One is shown in Electrical Room 157, which works for the East side of the clearstory. It is proposed that the second one be put in the Janitor Closet 121A on the West side of the clearstory. This will simplify conduit runs and keep conductor lengths shorter. It is proposed that the Cell Tower Dialer be installed above the drop-in ceiling of the Men's Dressing Room 141. This location would be accessible for servicing as well as in a location to have good Cell Tower reception. See attached drawing. |  | Envision Engineering is ok with the proposed locations, however confirm that the location for the zone expander (and any associated conduit/boxes) remains accessible, but is out of the way of any other items/storage and away from the sink in the janitorial closet. Cellular dialer to be located at an easily accessible location above the ceiling. A label may be needed at ceiling access panel to identify its location above. ¦ |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/17/2021 |  |  |  |  | Closed | 03/24/2021 | 03/31/2021 | 03/23/2021 | 03/23/2021 | 03/17/2021
1008 |  | 0 |  |  | Request for Information | A1 Sheer wall Portal and door openings for the North Additi | I will list the doors by number, needed opening size and current opening size: Door – 111. Needs to be 45” x 9’ – 6”. Current opening size is 42” x 8’- 8”. Door – 111A. Needs to be 45” x 9’- 6”. Current opening size is 41” ¾ “ x 8 ‘ – 8”. Portal – 146A. Needs to be 69 “ x 10’ – 6 “. Current opening size is 60 “ x 9’ – 10”. Door – 148B. Needs to be 45” x 9’ – 6”. Current opening size is 41 ½ “ x 8’ – 11 ¾ “. Door – 148A. Needs to be 45’ x 9’ – 6 “. Current opening size is 41 ½” x 8 ‘ – 11 ¾ “. |  | Based on previous conversations between the project team, it is ARW's understanding that the only door opening that needs the concrete opening cut wider is for opening 146A. This door will have 1-1/2" of concrete cut from each side of the opening and will be cut taller as well. This will allow the reinforcing jamb bars to remain in the wall and not be cut out. Westland had this wall scanned and verified the locations of the rebar. |  |  | High | Camron Walker | Westland Construction, Inc. | Structural Engineers |  | 03/17/2021 |  |  |  |  | Closed | 03/22/2021 | 04/15/2021 | 04/01/2021 |  | 03/17/2021
1009 |  | 0 |  |  | Request for Information | Chandelier Lifts 4th floor Controls Location | We need a location to install the controls for the chandelier hoists on the 4th floor. | Install the controls in the side wall below the pulpit walkway as shown on the attachment. This location gives a clear view on the chandeliers as they raise and lower, and is not easily seen and will be unobtrusive. | Envision is OK with the proposed switch locations as long as owner/CRSA is OK with them. We may want to try to somewhat conceal them under the benches a bit. ¦ Chandelier hoists are omitted on the fourth floor. See CCD 19R.7. ¦ ¦ Please see the response from Envision Engineering. |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/17/2021 |  |  |  |  | Closed | 03/24/2021 | 04/01/2021 | 03/31/2021 | 03/31/2021 | 03/17/2021
1010 |  | 0 | 230000, 260000 | M101, EP101, MP101, AE121 | Request for Information | Electrical Room 157 Clearances | Drawing M101, Electrical Room 157 indicates fan coil FC-1-27 to be installed. This fan coil is a below ceiling mounted unit with chilled water and condensate piping attached. Electrical drawings EP101 indicates panels, transformers and wall mounted gutters to be installed in this room. Architectural drawing AE121 indicates a 10' ceiling height. Due to the amount of electrical and mechanical components to be installed in this room there are currently clearance issues within the space. | Please advise if it be acceptable to raise the ceiling height to 12' in this electrical room to accomodate the mechanical and electrical components and eliminate the installation conflicts. See attached clouded drawings for reference. | Envision Engineering is ok with raising or eliminating the ceiling in this electrical room. Lighting fixture would need to be chain hung if ceiling is eliminated. ¦ Please see comments below from Envision Engineers. Ceiling the electrical room may be omitted. Gyp. board at the top of the wall needs to extend top the bottom of the roof deck if no ceiling is being provided. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 03/17/2021 |  |  |  |  | Closed | 04/02/2021 | 04/01/2021 | 03/31/2021 | 03/23/2021 | 03/17/2021
1011 |  | 0 |  |  | Request for Information | Confirm 028C Hardlid | 028C calls out for a grid lay-in ceiling. The concern is, there is a millwork item for the Veil curtains that attaches to the ceiling. Can we change this room ceiling to a hard lid and add wood backing for the millwork. --- Email Response: Jay, This does need to be a gypsum board ceiling and ½” plywood backing is acceptable. Thanks. Kyle Welch ¦ Project Manager 720 S. River Rd. Bldg. D Suite 2100B, St. George UT 84790 O: 435.673.7362 Ext. 110 C: 435.229.2906 |  | Confirmed. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/17/2021 |  |  |  |  | Closed | 03/24/2021 | 03/19/2021 | 03/17/2021 |  | 03/17/2021
1012 |  | 0 |  |  | Request for Information | 4th Floor Motion Sensors in Vestibules | No dimension is given for the Motion Sensors in the 4th floor vestibules 409 and 411. | It is suggested that the Motion Sensors be installed mirror image of the Speaker/Strobes. This would locate the Motions the same distance off center to the west as the Speaker/Strobes are to the East. This layout would keep the ceiling layout symmetrical. | Suggestion is confirmed per meeting 03/24/21. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/18/2021 |  |  |  |  | Closed | 03/25/2021 | 03/31/2021 | 03/24/2021 | 03/23/2021 | 03/18/2021
1013 |  | 0 |  |  | Request for Information | D-44 Medallion Clarification | The detail on B3/AE552 shows a reflected view of the D-44 medallion but does not have a section view of this medallion like the other medallion types. Attached is a photo of the existing medallion that we have scanned to create the new medallion off of. The center of the medallion is not fully intact and we need to know what size hole to put in the center of the medallion to allow for the lighting fixture. All other medallions have a flat spot and a hole. Please provide us with information of what needs to be provided for this medallion. |  |  | CRSA ARCHITECTURE |  | Medium | Dustin Williams | Unlimited Designs Inc. | CRSA ARCHITECTURE |  | 03/18/2021 |  |  |  |  | Forwarded | 03/25/2021 |  |  | 03/23/2021 | 03/18/2021
1014 |  | 0 |  |  | Request for Information | Valve box location | Melissa with CRSA ask if the installed valve boxes west of the fire line can be move so that they head west. We need direction on how to proceed as we have installed the boxes per plan and this is a deviation of that plan. Thanks |  | We have answered RFI 1014 as well as an RFI regarding missing irrigation information around the visitor's center. Please see narrative and attachments. ¦ |  |  | Medium | Rob Stratton | Stratton & Bratt Landscaping | Landscape Architects |  | 03/18/2021 |  |  |  |  | Closed | 03/25/2021 | 03/31/2021 | 03/26/2021 | 03/23/2021 | 03/18/2021
1015 |  | 0 |  |  | Request for Information | D-44 Medallion integration into adjacent drywall | The D-44 medallion shown on B3/AE552 will be brittle and fragile if cast without a solid backing to it. We propose a square or circular backing plate that is 5/8" thick that can more easily tie into the surrounding gyp ceiling or plaster ceiling. Is this acceptable? Is round or square preferred? For this to work as we propose, the drywall will have to be left out in this area, or the plaster removed to allow access to meet the same plane that the medallion is tying into. Can this be accommodated? |  |  | CRSA ARCHITECTURE |  | Medium | Dustin Williams | Unlimited Designs Inc. | CRSA ARCHITECTURE |  | 03/29/2021 |  |  |  |  | Forwarded | 03/25/2021 | 03/29/2021 |  | 03/29/2021 | 03/18/2021
1016 |  | 0 |  |  | Request for Information | Data and Outlet in Room 148 | Where should we locate the Data and Outlet devices on the West wall of Instruction Room 2, Room 148? There isn't enough room between the inner studs framing the insides of the diffusers to install even 1 box. | We could either put both devices to one side of the outside of the diffusers, or put one to either side of the diffusers. Either way we would put them as close to the diffusers as possible. The furniture plan shows a couch going in front of them, so aesthetically they wouldn't be visible either way. Please see attached drawings. | Shifting the power/data to one side of the diffuser is acceptable to Envision Engineering. Keeping them together is our preference. ¦ |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/18/2021 |  |  |  |  | Closed | 03/25/2021 | 03/31/2021 | 03/23/2021 | 03/23/2021 | 03/18/2021
1017 |  | 0 |  |  | Request for Information | Lobby 218 south lowered ceiling can light layout | There is a large ceiling beam that won't allow the can lights to be installed as originally shown on the RCP. | As per conversation with Kyle Welch it is proposed that 2 more can lights be added, and a new can light pattern be adopted. See attached drawings for clarification. This will likely incur a cost increase. | See CCD 136 showing the 2 additional lights and respacing. |  |  | High | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/19/2021 |  |  |  |  | Closed | 03/26/2021 | 03/31/2021 | 03/30/2021 |  | 03/19/2021
1018 |  | 0 |  |  | Request for Information | Crown Molding Cel. Rm. 218 | 1- We were informed by Kyle Welch with CRSA that there will be crown molding on the lower ceiling/south wall of Lobby 218. We need dimensions of the crown molding in order to create an accurate lighting layout. The current lighting layout won't work due to existing framing constraints. 2- Our understanding is that there will be no crown moldings on the East or West walls of room 218. If this understanding is incorrect please let us know. 3- Will there be crown molding on the north wall of 218? If so we need to know that for future lighting layout. If there is, we will assume it will be the same at the crown molding on the South wall unless told otherwise. |  | There is no crown in room 218 except the rope detail at the barrel ceiling portion. Please center lights between the south wall and entablature per our meeting on earlier this week. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/19/2021 |  |  |  |  | Closed | 03/22/2021 | 03/31/2021 | 03/26/2021 | 03/19/2021 | 03/19/2021
1019 |  | 0 |  |  | Request for Information | Instruction Room Pew Base Material | Can you confirm what the material is for the pew bases in Instruction Rooms 208, 209, 210, 211? There is no reference in the floor plan or in the room elevations to a detail calling out the material for the pew base. Thank you, Global Stone and Tile |  | This base is supposed to be stone base. Global stone is providing Ariston White marble. ¦ |  |  | High | Connor Cooper | GLOBAL STONE & TILE LLC | Interior Designer |  | 03/19/2021 |  |  |  |  | Closed | 03/22/2021 | 03/31/2021 | 03/30/2021 | 03/23/2021 | 03/19/2021
1020 |  | 0 | 230000 | M101 | Request for Information | HVAC air balance at Waiting Room area 109 | Drawing M101, Waiting area 109 indicates qty of 18 CD-7 grilles with 180cfm each for a total supply air of 3,240cfm. A qty of 6 SWR-1 grilles with 385cfm each for a total return air of 2,310cfm are shown. It appears this area might be short on return air capacity? Adjacent Storage Room 108A and 108B have 1 supply grille at 50cfm and 2 return grilles at 250cfm each. Should the return grilles shown serving storage rooms 108A and 108B be serving the Waiting area 109 instead? | Please advise if there is a discrepancy between the return grilles shown serving the waiting area 109 and the storage rooms 108A and 108B. See attached clouded drawing for clarification. | There is no discrepancy. Waiting 109 is returning 500 CFM through each storage room. This is to help dilute and alleviate any odors from the shoes and coats being stored there. ¦ |  |  | Medium | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/19/2021 |  |  |  |  | Closed | 03/26/2021 | 03/25/2021 | 03/23/2021 | 03/23/2021 | 03/19/2021
1021 |  | 0 |  |  | Request for Information | 500 S Gate Asphalt | The 500 South gate curb and gutter has a D arch bridge pour in for vehicles to cross. The D arch bridge has an edge because of the design. Around the sight asphalt has been built up to accomidate the D arch design and smooth out the edge created from the concrete pour. Is it the intent that follow what has been done around the sight to resolve the tripping edge the concrete creates? How much asphalt needs to be cut out to create an approach to the 500 south gate that is acceptable. Picture 1 and 2 are examples around the sight Picture 3 is the 500 south condition |  | Maintain a minimum of 5% slope. If the concrete is 4" higher than the asphalt would need to come out 6.67' from the edge. Feather the ashpalt out. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 03/19/2021 |  |  |  |  | Closed | 03/26/2021 | 04/01/2021 | 04/01/2021 | 03/23/2021 | 03/19/2021
1022 |  | 0 | 230000 | M105, M603 | Request for Information | Register CD-6 at level 4 barrel ceiling | Drawing M105, level 4 ceiling indicates installation of HVAC registers CD-6 at the barrel ceiling. Drawing M603, register schedule calls out for the CD-6 register to include a tapered neck for means of connection. This type of connection will require an increase of 3 1/2" inches in overall existing opening dimensions due to the type of construction of the existing ceiling material. It has come to our attention that the design team does not want us to cut openings larger than the existing openings current dimensions. | Please provide an alternative HVAC register/grille with a square/straight neck so that modifications to the existing ceiling material are not required. See attached for clarification. | An alternative would be to provide a Titus 1700L grille core with a Titus TRM plaster ceiling frame for each diffuser location. The TRM frame would allow for the 1700L core to be inserted and then rest on the frame, similar to a t-bar ceiling grid. The TRM would need to be custom fabricated for the existing 26x16 openings. Standard sizes are only 24x24. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 03/22/2021 |  |  |  |  | Closed | 04/02/2021 | 04/01/2021 | 03/31/2021 | 03/23/2021 | 03/22/2021
1023 |  | 0 |  |  | Request for Information | Fire Rated Man Doors at Stair 3 | Clarify final details of fire rated man doors at stair 3. Doors 501A, 401A, 301A, 201A, 184B, 052 | See communications between Fetzers and Scott Gilberg regarding fire rated door issues. | I can't see the emails you are referencing. Will you please attach the email you are referring to. | Paul Burningham | Fetzer`s Inc. | Medium | Paul Burningham | Fetzer`s Inc. | Westland PE’s |  | 03/22/2021 |  |  |  |  | Responded | 03/29/2021 |  | 03/23/2021 |  | 03/22/2021
1024 |  | 0 |  | See door schedule | Request for Information | Doors and Jambs east towers radius stairs | The following doors and jambs have been listed as historic doors to be reused. These jambs are removed and I do not believe these doors exist at Environmental Eagle either. Please clarify if these doors will need to be made new and provide the details for these doors, type, size, detail of jambs, etc. 063B, 063C, 224, 225, 226, 227, 330B, 329B, 413, 414, 412, 415 |  |  | CRSA ARCHITECTURE |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 03/22/2021 |  |  |  |  | Forwarded | 03/29/2021 |  |  | 03/23/2021 | 03/22/2021
1025 |  | 0 |  | FP-0801-WESTLAND & FP-0161-WESTLAND | Request for Information | Mulberry Leaf Motif for NORTH and EAST fountain bowls | Please provide us with images and approximate size for each mulberry leaf, for the mulberry leaf motif that is to be incorporated into the perimeter edge of the two large fountain bowls (NORTH & EAST fountains). |  |  |  |  | Medium | Mark Gabriele | Artisan Granite, LLC | Landscape Architects |  | 03/23/2021 |  |  |  |  | Closed |  | 03/23/2021 |  | 03/23/2021 | 03/23/2021
1026 |  | 0 |  |  | Request for Information | Additional Stone Location for North Addition | Do we need to add stone base in the locations marked in purple in the attachment (locker ends primarily)? See attached. |  |  | Interior Designer |  | High | Camron Walker | Westland Construction, Inc. | Interior Designer |  | 03/23/2021 |  |  |  |  | Forwarded | 04/15/2021 |  |  | 03/24/2021 | 03/23/2021
1027 |  | 0 |  |  | Request for Information | Type F Window Framing vs. Type E Windows | Carter spoke to Kyle from CRSA on-site on Friday, 03-19-2021 about the Type F window framing in the North Entry Vestibules framing height verse the Type E windows in the precast panel, Note they area at two different elevations. The type F window in this location are not seen from inside the Recommend area. We need to write an RFI so Kyle can give us direction to frame them to the E type window elevation in the Vestibules. |  | The type 'F' windows need to be framed the same height of the windows in the precast wall. |  |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 03/23/2021 |  |  |  |  | Closed | 03/30/2021 | 03/31/2021 | 03/23/2021 |  | 03/23/2021
1028 |  | 0 |  | A5/AE4113 | Request for Information | First Aid Casework Rm 124 Drw A5/AE4113 | 1. Redline drawings change the quatrefoil to fit within the 3” stile. Attached is a revised drawing showing the quatrefoil place within the 3” stile. Notice the quatrefoil looks out of balance with the casework. Please clarify if the direction given in the redline drawing is the direction Fetzers is to take. 2. I cannot change the size of the cutout of the soffit insert from 3.25” to 2.5” due to the size of the tooling already purchased for this project. The size of this soffit insert is consistent with all soffit inserts of wood casework. 3. There is a red line on the returned redlines with no indication as to what it is. There is no cross section indicating what this line represents of grain direction. Please clarify. 4. Per ASI 116 are we to understand the grain direction in the soffit panel is to run vertical and not horizontal? 5. A1/AE 590 indicates the insert panels on the doors are to be crotch mahogany. We have no crotch mahogany on the project and are shop drawing we indicated this to be African mahogany. Please clarify if these panels are to remain as drawn or is this veneer to be crotch mahogany? |  | Disregard previous redlines. Match this crown (soffit) to the rest of the millwork crowns in the project. 3.25" is okay. Also all quatrefoils to be 3.25" to match rest of project Disregard Yes, run all soffit panels grain vertically as discussed on site visit 4/5/21 Mahogany to match project material (African Mahogany is acceptable) ¦ |  |  | High | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 03/23/2021 |  |  |  |  | Closed | 04/02/2021 | 04/13/2021 | 04/09/2021 | 03/23/2021 | 03/23/2021
1029 |  | 0 |  | Fetzers drw 435.1 Submittal 064023.20.00 | Request for Information | Training Room Casework Redline Questions Fetzers drw. 435.1 | 1. Provide additional details for the Training room casework. 2. End view A3/435.1, shows added cross rail and detail A shows a step in the trim but no dimension is given as how far the added cross rail is to protrude from the face of the cabinet. 3. I f a stile is added to the upper cabinet and is to protrude from the end panel an upper rail needs to be added or the crown molding will not work. 4. Provide a cross section through the end of the cabinet. |  | Proceed with direction given during site visit on 4/5/21 (see attached sketch) ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 03/23/2021 |  |  |  |  | Closed | 03/30/2021 | 04/13/2021 | 04/09/2021 | 03/29/2021 | 03/23/2021
1030 |  | 0 |  |  | Request for Information | Curb and gutter at 500 S and 200 E | Per the field conversation about the replacement curb and gutter with Paul Mogle. Paul is going to provide a detail for the curb and gutter replacement like the intersection by the visitors center that has a grate covering the underground drain pipe. |  | This can be closed out. No detail is needed. See comments. ¦ |  |  | Medium | Zac Givens | Westland Construction, Inc. | Civil Engineers |  | 03/24/2021 |  |  |  |  | Closed | 03/31/2021 | 04/15/2021 | 04/14/2021 | 03/29/2021 | 03/24/2021
1031 |  | 0 |  |  | Request for Information | DL-1 Voltage | The dock leveler DL-1 at receiving 125 is 480V on the electrical drawings feeding out of panel H1M0B, but the mechanical submittals (see attached) call out 208V. The conduit has already been run to the 480V panel. If the voltage changes we will need to run the circuit to a 208V panel and purchase a new 208V 3-pole breaker. Please advise. |  | Envision will update power circuiting in future CCD-147 for change in product voltage ¦ I decided to update this to include the email from Scott for reference. _____________________ Camron, Per discussion today about RFI 1031 regarding dock leveler power, the designed product was for 480V, 3 phase power which is what is shown for circuiting on the electrical drawings. In reviewing the product submittal, it looks like there is an option for 480V, 3phase power even though it calls for 208V, 3phase. We would like to add a comment to the submittal to require the 480V, 3 phase power so that it matches up with what is designed and avoids the electrical changes. Our response to RFI 1031 would need to be updated as well, as this discussion to note the submittal occurred after the RFI was responded to. Let me know if you have any questions. Thanks, Scott Hardy D. 801.924.5547 C. 801.913.5278 |  |  | High | David Barney | Wilkinson Electric Inc | Electrical Engineers |  | 03/24/2021 |  |  |  |  | Closed | 04/01/2021 | 04/09/2021 | 04/09/2021 | 03/29/2021 | 03/24/2021
1032 |  | 0 |  |  | Request for Information | Door 148C to room 148A Closet | This door has a lock only. Hardware Group 52. Typically I have always seen this door in other temples with the centerline of the lock placed below the height of the chair rail or below the height of the back of the chairs so as not to bring attention to this door. Currently the lock on this door is placed at the standard height of all other doors. Does the center line of this lock at door 148C need to be placed lower than normal and if so provide a location of this lock? |  | Thank you for bringing this tour attention. I have not specified the height of the lock. What is the typical height you see? I am attaching a photo of the chair in the room. It is 35" high and has an open back. Do you need more specific measurements? If so how soon? We hope to have shop drawings soon on these chairs. ¦ Discussion was had amongst the interior design team regarding this question. Direction is that this door and it hardware to be provided as called for in bid set. It is intended that this door looks like all the other doors. ¦ |  |  | Medium | Paul Burningham | Fetzer`s Inc. | CRSA ARCHITECTURE |  | 03/24/2021 |  |  |  |  | Closed | 03/31/2021 | 04/13/2021 | 04/07/2021 | 03/29/2021 | 03/24/2021
1033 |  | 0 |  |  | Request for Information | Roller Shades in Instruction Rooms | The roller shades in the instruction rooms need to be mounted on a flat surface. How should these be mounted? Attachments: INSTRUCTION ROOM 5 WINDOW TREATMENT (suggestion) RB_HeavyDuty_Blockout_Diagram_2021 (this roller shade but motorized) | See the attached drawing from a similar project. We propose building out the splay so there is a flat surface for the first few inches and then starts to taper out. |  | CRSA ARCHITECTURE |  | Medium | Mark Lawrence | House of Drapery Inc. | CRSA ARCHITECTURE |  | 03/25/2021 |  |  |  |  | Sent | 04/01/2021 |  |  |  | 03/25/2021
1034 |  | 0 |  |  | Request for Information | Veneer Plaster | The paint in room 408 is peeling and could potentially cause delamination issues for the new plaster finish. Will you please provide us with some information on how to proceed? |  | an on-site discussion occurred (3-30-21) between CRSA and R Phillips to discuss this issue. R Phillips was instructed to provide a 'write-up' narrative, illustrating what is the most appropriate and best solution would be. This narrative will be reviewed and likely issued as a CCD at that time. ¦ A site visit may be required to review this concern. |  |  | High | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 03/25/2021 |  |  |  |  | Closed | 04/01/2021 | 04/01/2021 | 03/31/2021 | 03/29/2021 | 03/25/2021
1035 |  | 0 |  |  | Request for Information | VFD for CWP3 | Who is supplying the VFD for CWP3? The equipment schedule on EP601 indicates that it isn't existing, and that it is furnished by others. The schedule on M601 doesn't show it being supplied by the Mechanical contractor. See attached drawings. |  | In the mechanical drawings, there is no VFD scheduled or shown for CWP-03. The pump is connected to the bypass heat exchanger which does not require a VFD for operation. The VFD can be omitted from the electrical design. ¦ ¦ Brian, would you look at this? Per design coordination, we shows this as VFD by others (not electrician). Thanks, Scott |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | Brian Oswald | VBFA INC CONSULTING ENGINEERS | 03/26/2021 |  |  |  |  | Closed | 04/02/2021 | 04/13/2021 | 04/05/2021 | 03/31/2021 | 03/26/2021
1036 |  | 0 |  |  | Request for Information | Trench drain size and pattern | Confirm that the trench drain size for the north plaza are to remain the 4 inch size. Confirm that the trench drain size for the baptistry is to be 8 inch. Please provide radius and dimentions of the baptistry trench drains. In RFI 922 it calls out the trench drain pattern as the title wave but the plans call out double wave. Please confirm what pattern needs to be ordered. |  |  | Landscape Architects |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 03/26/2021 |  |  |  |  | Forwarded | 04/02/2021 |  |  | 03/29/2021 | 03/26/2021
1037 |  | 0 |  |  | Request for Information | Tower Added Lighting Needed | There is a level of the Historic Tower not shown on the drawings. There is no lighting shown for that space. Should light fixtures be added. The dome has no interior lighting shown. Should a small fixture be added, such as a Jelly Jar type fixture? There is another space inside of the tower near the hatch that opens to the roof of the 2nd level down from the tower. This area will be dark. Should a light fixture be added, such as a Jelly Jay type fixture? | Add light fixtures as shown on attached drawing. This will incur a cost increase. Please see the attached drawing. | In conversations with Eric, additional basic keyless socket with wire protection type lighting will be added to provide additional lighting in the upper tower to facilitate night time maintenance. Future revisions will be done for CCD-081R1. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 03/29/2021 |  |  |  |  | Closed | 04/02/2021 | 04/01/2021 | 03/31/2021 | 03/31/2021 | 03/29/2021
1038 |  | 0 |  |  | Request for Information | Chandelier Lifts for 4th floor | Will there be chandelier hoists for the 5 large chandeliers on suspended on the higher, barreled ceiling through the existing, historic medallions? | A conference call was held between myself (Matt Heaton) and three members of the staff of Dynapac Rotating Company (John Margetts, Jeremy Bingham, and Charlie Eves). After explaining the details of our particular needs they are confident that a chandelier hoist configuration can be built that will allow the power cord, hoist cable, and safety arrestor cable to fit together through the 1 1/8" diameter holes in the centers of the existing, historic medallions without any modification. Details of the outcome of the discussion are outlined on the attached drawing. They can be contacted with any further concerns or questions. | Hoists are not to be provided for the (5) chandeliers located in the barrel ceiling of the 4th floor. This is direction from the project owner and this specific direction has been issued in CCD 19R.7. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/29/2021 |  |  |  |  | Closed | 04/02/2021 | 04/01/2021 | 03/30/2021 | 03/30/2021 | 03/29/2021
1039 |  | 0 |  |  | Request for Information | Men's Dressing Outlet Move Confirming RFI | As per conversation with Kyle Welch and Carter Cluff on March 29, 2021 two outlets on the north wall of Men's Dressing Room 141 were moved. They were relocated to inside of booths, and under the booth seats and installed at a height of 15" AFF to center. See attached drawing for clarification. Please confirm that this is acceptable. |  | Moving the outlets under the benches in the stalls is acceptable. Please coordinate with the Metal locker & Dressing Compartment shop drawings for the bench heights. Place the outlet from the top of finish outlet plate 1" clear to the bottom of blocking support at the wall mounted benches. The east dressing stall outlet, (where bench is not mounted on the wall) can be standard height located on the wall per our site visit discussion. |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 03/30/2021 |  |  |  |  | Closed | 04/06/2021 | 03/31/2021 | 03/30/2021 | 03/30/2021 | 03/30/2021
1040 |  | 0 |  |  | Request for Information | Laundry Closet 028A lay-in to Hard lid Change | The change made in RFI 1011 from lay-in ceiling to hard lid presents some problems for the electrical and plumbing. 1-The compressor/chiller for the drinking fountains in Vestibule 025 and water line are already installed, as well as the power. The compressor will not be able to move all of the way out to the ceiling of the laundry room and stay within the maximum distance of 15' from the drinking fountain (P602, Electric Water Cooler Schedule Notes 3, 4). 2- There are numerous electrical J-boxes also installed above this ceiling. Changing this closet to a hard lid would necessitate relocating all of these items, and a cost would be involved. Even adding 1 or 2 access panels would not give good access to the compressor/chiller or the electrical J-boxes as they are currently installed. As a side note, the dimensioned layout for the light and sprinkler are in conflict with the hanger system as shown. Please see the attached drawings. | In the past the curtains were installed on rolling racks which facilitated pressing and hanging them, and then taking them up to the Veil Room to be changed out. Can this method be considered again in lieu of the fixed hanging system? The closet is large enough to house 2 rolling hanging racks. | CRSA is not familiar with a change calling for this ceiling to be changed from a 'lay-in' to hard lid. From what i can see, drawings still appear to call for a lay-in ceiling. and yes......the light in discussion will likely need to be adjusted to fit in the room. please adjust ceiling grid and light placement accordingly. ¦ It was decided that an owner provided rolling drapery cart is going to be used and the previously proposed ceiling mounted drapery hanger system and the plywood backing is not needed. Because of this change the lay-in ceiling is to be installed per the previous original design intent. ¦ Please review the referenced RFI 1011 and the response from Kyle Welch concerning changing from lay-in to hard lid. |  |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/09/2021 |  |  |  |  | Closed | 04/07/2021 | 04/14/2021 | 04/14/2021 | 03/31/2021 | 03/31/2021
1041 |  | 0 |  |  | Request for Information | Medallion Installion Option - C-48, C-48L, and D-44 | Please see attachment. Need direction on C-48, C-48L, and D-44 molds. In order to create the "owl head" design as part of a full medallion, we need to put it on a flat backing pad of GFRG that is 5/8" thick. This hold the design together. Please advise if this is acceptable. | We understand that this will require coordination between drywallers and Unlimited Design, but we feel it is the only way to the acheive the design. Please advise. |  | CRSA ARCHITECTURE |  | Medium | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2021 |  |  |  |  | Forwarded | 04/07/2021 |  |  | 04/12/2021 | 03/31/2021
1042 |  | 0 |  |  | Request for Information | D-44 Medallion - Center Light Fixture Opening Dimension | After scanning medallion D-44, it is unclear what the center opening dimension must be for the light fixture. Please advise center opening dimension for medallion D-44. We will need this dimension in order to begin fabrication. Please advise ASAP. UPDATE: After a discussion with Matt Heaton this round opening needs to be 4 1/4". Please advise. He mentioned this also relates to RFI 974 because he needs to know the thickness too so he knows how to mount the 4 1/4 inch box. |  |  | CRSA ARCHITECTURE |  | High | Aaron Bowers | Pete King Commercial | CRSA ARCHITECTURE |  | 03/31/2021 |  |  |  |  | Sent | 04/09/2021 |  |  |  | 03/31/2021
1043 |  | 0 |  |  | Request for Information | Stone graining | As Delta is starting to slab material, they are noticing some prominent graining in some of the blocks. Is there a preference in grain direction for the site caps? (See attached). |  | Please ensure the direction of the grain runs parallel to the wall. Refer to attached diagram. ¦ | Bob Durrant | IMS Masonry Inc. | Medium | Bob Durrant | IMS Masonry Inc. | Landscape Architects |  | 03/31/2021 |  |  |  |  | Responded | 04/16/2021 |  | 04/15/2021 | 04/09/2021 | 03/31/2021
1044 |  | 0 |  | ES200, ES202 | Request for Information | Driver Location for Monument Sign Lighting | This is a follow up to RFI #864. Zac Givens suggested we put these drivers for the monument sign lighting in a ground box to hide them and have a cleaner look. The attached is our proposed ground vault and direct burial/outdoor rated driver. However, to do this would incur an additional cost of around $2,500. Should we submit a proposal to do this or go with the locations advised in RFI #864? |  |  | Landscape Architects |  | Medium | David Barney | Wilkinson Electric Inc | Landscape Architects |  | 04/02/2021 |  |  |  | 2500.00 | Sent | 04/16/2021 |  |  |  | 04/02/2021
1045 |  | 0 |  |  | Request for Information | Chandelier hoist controls locations for 210 & 211 | Are the proposed locations for chandelier hoist controls in rooms 210 and 211 acceptable? | Please see the attached drawings for the proposed locations. They are near doorways in the back of the rooms where there are no other devices or equipment shown. They are proposed to be installed at 48" AFF to center and 8" to center horizontally from door casings or splays, as is typical. These locations were coordinated with Brian Chandler, Temple TFM. |  | CRSA ARCHITECTURE |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/05/2021 |  |  |  |  | Forwarded | 04/12/2021 |  |  | 04/12/2021 | 04/05/2021
1046 |  | 0 |  |  | Request for Information | Sconce Lighting Dimensioned Layout, Room 218 | Can we get a dimensioned layout for the sconces on the East and West walls of room 218? There is a clash with the LVL's and the boxes for the sconces on the West wall. Please see the image from BIM. Is there a mirror behind the sconces on the East wall? Please see attachments for clarification. |  |  | CRSA ARCHITECTURE |  | Medium | Matt Heaton | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/05/2021 |  |  |  |  | Forwarded | 04/12/2021 |  |  | 04/13/2021 | 04/05/2021
1047 |  | 0 |  |  | Request for Information | North Addition Column Fireproofing | Fireproofing around various columns in the North Addition doesn't fit within the stud cavity (see the attached for a few examples). Please advise. | We propose replacing the spray fireproofing with intumescent fireproofing. NOTE: There would be a cost to scrape the spray fireproofing and to clean the column to an acceptable level for painting with the added intumescent fireproofing. |  | CRSA ARCHITECTURE |  | High | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/06/2021 |  |  | 0.00 |  | Sent | 04/09/2021 |  |  |  | 04/06/2021
1048 |  | 0 |  |  | Request for Information | Deco Lighting Bulb Discontinued - Substitution Satco C11 LED | The Tamarac E12 lamp specified for much of the decorative lighting for St George Temple has been discontinued. We are suggesting an alternate: Satco S11371. Spec sheet attached. |  | We contacted the manufacturer of the specified lamp and discovered that it has been discontinued without a replacement. We searched other manufacturers data to find a 600-Lumen replacement, but we did not find one. We could not find any alternate lamps that produce more than 500-Lumens; however, we did find several that are more efficient than the proposed SATCO Products, Inc., S11371 lamp (90.9 LpW). We would therefore recommend that the most efficient of these lamps be used instead; PL&T Solutions, PLT-11830 lamp (111.11 LpW). |  |  | Medium | Leeann Latsch | Remains Lighting | Electrical Engineers |  | 04/06/2021 |  |  |  |  | Closed | 04/13/2021 | 04/13/2021 | 04/08/2021 |  | 04/06/2021
1049 |  | 0 |  |  | Request for Information | Finish Materials in Landscape Shed - CCD 066R1 | Global Stone and Tile is listed as suppliers/installers for the wall tile and base pavers in the Landscape Shed; however, there is no specification for materials in the shed. Can you please specify the following materials: Wall tile (we're assuming WT3) Base tile under wall tile (we're assuming BT4) Countertop (we see that butcher block is specified, please confirm this is correct) Threshold (we see an aluminum threshold is specified, please confirm this is correct) Thank you, Connor | WT3- Daltile Rittenhouse Square, Semi-Gloss Field Tile, Color: 0766 Elemental Tan, Matte Finish, 6x6 BT4- Daltile Rittenhouse Square, Color: 0766 Elemental Tan, Matte Finish, Cove Base 6x6 |  | Interior Designer |  | High | Connor Cooper | GLOBAL STONE & TILE LLC | Interior Designer |  | 04/06/2021 |  |  |  |  | Forwarded | 04/16/2021 |  |  | 04/07/2021 | 04/06/2021
1050 |  | 0 |  |  | Request for Information | HSS Anchor Bolt Embed HC / H1 | At the Historic Building, level 0.5, the anchor bolts for the HSS columns at HC and H1 were not installed prior to concrete pour. Please advise if these anchors bolts can be drilled and epoxied with screen tubes. |  | Yes. These anchors can be post installed. ¦ |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 04/06/2021 |  |  |  |  | Closed | 04/13/2021 | 04/12/2021 | 04/06/2021 | 04/06/2021 | 04/06/2021
1051 |  | 0 |  |  | Request for Information | Wall Type at Room 218 | Please provide wall type for the west wall of room 218. |  |  | CRSA ARCHITECTURE |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/06/2021 |  |  |  |  | Forwarded | 04/15/2021 |  |  | 04/13/2021 | 04/06/2021
1052 |  | 0 |  |  | Request for Information | Epoxy Coating at Sump Vault South Mechanical 043 | UPDATE: See the suggested product below. (Note: There will be a cost for this waterproofing). Should the exterior of the sump vault at south mechanical 043 be epoxy coated? |  | After discussion with VBFA we feel it would be best to epoxy coat the exterior of the sump. ¦ proposed Bitumastic 300 product is acceptable. and yes, please have US mech apply the waterproofing........specifically bob. |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/06/2021 |  |  |  |  | Closed | 04/15/2021 | 04/12/2021 | 04/12/2021 | 04/12/2021 | 04/06/2021
1053 |  | 0 |  | 1/P102 | Request for Information | Restroom Floors Room 215 & 216 | Should the restroom floors 215 and 216 be recessed to received floor tile and allow slope to the floor drains? | Create 2 inch recess by removing existing flooring at these two restrooms, cutting top 2 inches of existing floor joists, sister LVL's to existing floor joists, and install 3/4 inch plywood decking. | It is acceptable to replace the joists under the restroom with 1-3/4” x 9-1/2” LVL similar to the restrooms at levels 3 and 5 to accommodate the thick set tile and provide the 2” recess. Please confirm with CRSA and the owner that this is acceptable, and that is the direction needed to pursue. ¦ please proceed with direction and approval given by arw for this RFI ¦ ¦ ¦ please advise if the direction given by Zac is acceptable, and if we are to proceed in this direction. |  |  | High | Jason Fullmer | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/06/2021 |  |  |  |  | Closed | 04/15/2021 | 04/14/2021 | 04/13/2021 | 04/13/2021 | 04/06/2021
1054 |  | 0 |  |  | Request for Information | Historical stair dimensions | ASI 104 gives the elevation of the bottom of the historical stairs. In our submittal for this area, (see attached) we have requested additional information. Please provide information so that drawings can be completed, and stone cutting can start. |  |  | CRSA ARCHITECTURE |  | Medium | Bob Durrant | IMS Masonry Inc. | CRSA ARCHITECTURE |  | 04/07/2021 |  |  |  |  | Forwarded | 04/14/2021 |  |  | 04/13/2021 | 04/07/2021
1055 |  | 0 |  |  | Request for Information | Replace the mesquite trees and adjusted irrigation needs | How should Stratton and Bratt proceed with the replacement of the Mesquite trees? How should the irrigation be adjusted around these trees? |  | Please see the attached for further direction on irrigation adjustments to all Mesquite trees. Also attached is a plan showing the two locations where the Mesquite trees will either not be replaced or not be planted. ¦ |  |  | High | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 04/07/2021 |  |  |  |  | Closed | 04/15/2021 | 04/13/2021 | 04/13/2021 | 04/13/2021 | 04/07/2021
1056 |  | 0 |  |  | Request for Information | Re: PR_17 - Wood Species of Mahogany and Cut | Please clarify wood species of mahogany and cut as it relates to PR_17: Mahogany Sapele ? African Mahogany? Or other? Rift Qtr or plain sawn? |  | Provide plain sawn and quarter sawn pricing. Provide pricing for both Sapele and African mahogany. What wood species is more accessible to you? |  |  | Medium | Danny Groves | New Holland Church Furniture | Interior Designer |  | 04/07/2021 |  |  |  |  | Closed | 04/14/2021 | 04/14/2021 | 04/14/2021 |  | 04/07/2021
1057 |  | 0 |  |  | Request for Information | Level .5 Mechanical Openings | Please give us direction on what’s expected as far as rebar details/engineering on the attached mechanical openings. How far up into the floor joists are we placing concrete, are we going into the joists... the mechanical openings themselves will be into the joists. Please give us a detail/design on how you would like these built and reinforced. |  | Nothing special needs to be done except build the new concrete header up flush to the bottom of the joist. We recommend adding piece of treated lumber (if it fits) or a sheet of tar paper between the top of the concrete and bottom of joist to protect the joist. The concrete beam can be reinforced and built the same as in 8/S240. ¦ Please do not close out the RFI as of yet. Chopper is going to review again, but he is thinking that the openings Cobe needs are going to go right up to the floor joist and there will not be any room for concrete to go up over the top, but as I said he needs to confirm. If this is a solution Westland will need to provide the treated lumber and or the tar paper. We may need to set up a walk with Jason, Cobe and Chopper | Structural Engineers |  | High | Stormy Carlisle | Innovative Concrete LLC | Structural Engineers |  | 04/08/2021 |  |  |  |  | Responded | 04/15/2021 |  | 04/12/2021 | 04/09/2021 | 04/08/2021
1058 |  | 0 |  |  | Request for Information | CCD 139-SECURITY BOLLARDS | Please provide a removable bollard detail for the new bollards added in CCD 139. |  |  | CRSA ARCHITECTURE |  | Medium | Stormy Carlisle | Innovative Concrete LLC | CRSA ARCHITECTURE |  | 04/08/2021 |  |  |  |  | Forwarded | 04/15/2021 |  |  | 04/13/2021 | 04/08/2021
1059 |  | 0 | 230000 | M102, AE | Request for Information | Historic Level 2-HVAC Grille Clarification | Drawing M102 indicates multiple sidewall supply and return HVAC grilles. Some of these are provided with dimensioned locations shown on the Architectural drawings. Others have not. The grilles not provided with dimensions are as follows: Drawing AE4206, AE4208, AE4210, Stair S-5 AE389. Attached are clouded drawings indicating either missing cuts or grilles on the Architectural drawings. | Please provide dimension locations for these HVAC grilles as indicated. | Please see ASI #130 showing adjusted locations of mechanical grilles and dimensions. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | CRSA ARCHITECTURE |  | 04/09/2021 |  |  |  |  | Closed | 04/15/2021 | 04/15/2021 | 04/15/2021 | 04/12/2021 | 04/09/2021
1060 |  | 0 | 230000 | MPD100, M411 | Request for Information | HVAC Central Plant Existing Chilled Water Piping Size | Drawing MPD 100, mechanical room 035 indicates that the CHWS and CHWR piping connected to the existing chillers is to remain. Drawing M 411 indicates existing chilled water piping supply and return piping is 8" in size. Upon further field verification it has been discovered that both CHWS and CHWR existing piping serving the chillers reduces as it enters tee fittings and leaves mechanical room 035 and enters the existing chiller room overhead at/near the existing south double door. See attached drawings for clarification. | Please confirm that all CHWS and CHWR piping to include accessories and control valves are to be 8" in diameter. New control valves are currently sized 8", the existing chiller connections are 8" in diameter as well. | The 2 options available are: 1) Upsize the CHWS and CHWR piping connected to the chillers from 6" to 8". 2) Leave the existing 6" piping in place and change the control valves from 8" to 6". Either option is acceptable from a performance perspective. Since both options have similar timeframes for completion, the preference would be to go with the option that is least expensive (option 2). Please confirm final decision with the owner. ¦ |  |  | High | Justun Bylund | US Mechanical LLC | Mechanical Engineers |  | 04/09/2021 |  |  |  |  | Closed | 04/15/2021 | 04/14/2021 | 04/14/2021 | 04/12/2021 | 04/09/2021
1061 |  | 0 |  |  | Request for Information | Handrail vs Door Casing | There is a conflict between the handrail and the door casing in this location. Please advise. |  |  | CRSA ARCHITECTURE |  | Medium | Camron Walker | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/09/2021 |  |  |  |  | Sent | 04/15/2021 |  |  |  | 04/09/2021
1062 |  | 0 |  |  | Request for Information | Finish in Jan. 074 and Jan. 076 | In order to finish out Jan. 074 and Jan 076, it appears we need to add some wall framing. Please confirm. |  |  | CRSA ARCHITECTURE |  | Medium | Ryan Thomas | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/10/2021 |  |  |  |  | Sent | 04/19/2021 |  |  |  | 04/10/2021
1063 |  | 0 |  |  | Request for Information | East plaza bench pad elevations | The east plaza's slope transfers into the bench pads. -Should the bench pads slope be adjusted to flatten out so the benchs sit level? -The plans call out J bolts to be installed in the rat slab. To avoid layout conflicts between the bench bolts and paver joints we suggest to drill into the pavers after install. Please provide direction for bench pad slopes in the east plaza and bench attachment bolts. |  |  | Landscape Architects |  | Medium | Zac Givens | Westland Construction, Inc. | Landscape Architects |  | 04/12/2021 |  |  |  |  | Forwarded | 04/19/2021 |  |  | 04/13/2021 | 04/12/2021
1064 |  | 0 |  | 9/S222 | Request for Information | Concrete Infills at Deck Level 0.5 | Reference detail 9/S222. There are several openings the concrete deck at level 0.5 that will not be occupied with duct work. Please advise how we are to infill these openings between the bent plates. | Per discussion with Matt McBride, concrete on metal B decking supported by steel angle would suffice. Please confirm this is acceptable. | suggestion to provide metal deck, support angles and concrete infill is acceptable. please proceed. |  |  | Medium | Jason Fullmer | Westland Construction, Inc. | Structural Engineers |  | 04/13/2021 |  |  |  |  | Closed | 04/20/2021 | 04/13/2021 | 04/13/2021 | 04/13/2021 | 04/13/2021
1065 |  | 0 |  |  | Request for Information | Plaster to Window connection | The drawings show the windows having a grooves that will accept the plaster. The Windows that were installed don't have this groove. Will the groove be cut into the window frame? I installed a piece of "J" metal on one of the windows on Level 5, as a mock up. Please let me know as soon as possible which method we are going to use. |  | Please see the attached RFI regarding the plaster to window connection. |  |  | Medium | Clinton Phillips | R. Phillips Plastering LLC | Westland PE’s |  | 04/13/2021 |  |  |  |  | Closed | 04/20/2021 | 04/13/2021 | 04/13/2021 |  | 04/13/2021
1066 |  | 0 |  |  | Request for Information | Plaster Veneer | The Plaster Veneer on level 4 is starting to delaminate from the old plaster. There is a faulty layer of paint that has delaminated from the original plaster. We have done some investigation and have tried some experimental fixes. I don't feel comfortable with any of these nor can I provide a warranty against future failures. How should we proceed? Options: Demo all old plaster Demo down to failing paint layer Install metal lath over existing and proceed to install veneer plaster. Recommended Fix: I recommend that we install 2.5 metal lath over all plaster walls. This is the only way that I can guarantee that we won't have the delaminating problems moving forward throughout the building. |  |  | CRSA ARCHITECTURE |  | High | Clinton Phillips | R. Phillips Plastering LLC | CRSA ARCHITECTURE |  | 04/13/2021 |  |  |  |  | Forwarded | 04/16/2021 |  |  | 04/13/2021 | 04/13/2021
1067 |  | 0 |  |  | Request for Information | Lobby 218 - South, Lowered Ceiling Lighting Layout | In measuring the physical space for the lighting layout in Lobby 218, south, lowered ceiling, there is one decision to be made. The west wall is a different distance from center of the nearest window than the east wall is from the center of its nearest window. We need to decide which measurement off of the east walls to the row of can lights to use. Please see the measurements on the attached drawing for clarification, and confirm that the rest of the layout will work. | We may need a short conference call involving Kyle Welch, Scott Hardy, Matt Heaton, and Jason Fullmer with all of us looking at the proposed layouts and come to a consensus. | please keep the medallions/chandeliers centered or lined up with the windows on the south exterior wall, The medallions then to be the basis of laying out all other ceiling elements. please line up, center with, and provide as symmetry as possible using the medallion locations. a brief meeting prob a good idea. ¦ |  |  | High | Matt Heaton | Wilkinson Electric Inc | Electrical Engineers |  | 04/13/2021 |  |  |  |  | Closed | 04/17/2021 | 04/14/2021 | 04/14/2021 | 04/14/2021 | 04/13/2021
1068 |  | 0 |  |  | Request for Information | Verify 2' - 8" Door Widths | There are various 2' - 8" doors called out on the door schedule in the North Addition. We just want to verify that these are all correct. A good example of one that might be incorrect is the door into the recorder office (door 128). Please advise. |  |  | CRSA ARCHITECTURE |  | High | Carter Cluff | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/13/2021 |  |  |  |  | Sent | 04/16/2021 |  |  |  | 04/13/2021
1069 |  | 0 |  |  | Request for Information | Electrical Device Placement Areas 3&4 Annex 1st floor | Confirming that as per site walk with Kyle Welsh 3-25-2021 We were either directed or approved to make slight changes in device placement because of conflicts with framing. See Attachment for locations |  |  | CRSA ARCHITECTURE |  | Medium | Trask Johnson | Wilkinson Electric Inc | CRSA ARCHITECTURE |  | 04/14/2021 |  |  |  |  | Forwarded | 04/21/2021 |  |  | 04/14/2021 | 04/14/2021
1070 |  | 0 |  |  | Request for Information | Finish Above Roof Line on A1 Sheer Wall | Please confirm that per an onsite conversation with Jay and Scott that the wall finish above the roof line along gridline A1 sheer wall (Bride hallway 146) are to match wall finishes with the clerestory. |  |  | CRSA ARCHITECTURE |  | Medium | David Adams | Westland Construction, Inc. | CRSA ARCHITECTURE |  | 04/16/2021 |  |  |  |  | Forwarded | 04/22/2021 |  |  | 04/16/2021 | 04/16/2021
1071 |  | 0 |  |  | Request for Information | 4th floor chandeliers in barreled ceiling - hanging detail | Can we get a confirmation on using the hanging method as shown on the attachment? These chandeliers are the five type LF-A7 (A-3-24-51) that go on the 4th floor barreled ceiling. They weigh 189 lbs. Can we get a confirmation on the hanging detail for hanging chandeliers through the D-44 type medallion? The detail is shown on the attachment. We still need to know the thickness of the D-44 chandelier as clarified on the attachment. |  |  | Westland PE’s |  | Medium | Matt Heaton | Wilkinson Electric Inc | Westland PE’s |  | 04/16/2021 |  |  |  |  | Sent | 04/23/2021 |  |  |  | 04/16/2021